## Significant event descriptions
Year | Incident number | Industry sector | Personnel involved | Actual consequence | Potential consequence (Critical Risk) | Critical risk | Description of event
|  | Generation |  | No injury | Fatality |  | 4 March 2018, Maraetai 2 hydro power station - Members of public broke into secure area to go fishing
2018 | 01-2018 | Generation | Contractor | No injury | Fatality | Asset failure | 9 May 2018, Maraetai 1 hydro power station - Generator overspeed event while commissioning. The overspeed device tripped the unit at 140% speed, but the overshoot caused the unit to reach 160% of rated speed
|  | Generation |  | No injury | Fatality |  | 23 October 2017, Downstream of Lake Taupo Control Gates - Kayaker rescued from rock in Waikato River. Hydro Control not notified by Police during incident
2018 | 02-2018 | Generation | Contractor | No injury | Fatality | Confined spaces | 7 December 2017, Maraetai 1 hydro power station - Occupational diver failed breathe alcohol test
2018 | 03-2018 | Generation | Employee | No injury | Fatality | Driving | 17 October 2017, Public road. Mercury generation employee had to take evasive action, when an oncoming vehicle (driven by member of public) crossed the centre line
2018 | 04-2018 | Generation | Employee | No injury | Fatality | Driving | 7 September 2017, Public road. Mercury generation employee had to take evasive action, when an oncoming vehicle (driven by member of public) crossed the centre line
2018 | 05-2018 | Retail | Employee | Minor injury | Fatality | Driving | 2 July 2017, Public road. Mercury retail employee suffered minor injuries, when the vehicle they were driving was struck by an oncoming vehicle (driven by member of public) that crossed the centre line
2018 | 06-2018 | Generation | Employee | No injury | Fatality | Asset failure | The CHF on the wellhead had two threaded side outlets that were filled with cast threaded bull plugs. These plugs were exposed to wellbore pressure. The well in question had been off pressure for a number of years and was recently abandoned (a few months back). During the post-abandonment wellhead removal, during hammering to the top face of the CHF, one of the plugs just fell off. It is reported that it had not been hit or knocked. The failure was a fracture of the steel surface part-way down the engaged threaded section. If the well had been under pressure, the bull plug could have turned into a high speed projectile.
2018 | 07-2018 | Generation | Employee | No injury | Fatality | Asset failure | On Monday afternoon 16 October 2017, CEL was informed by Nalco representative that the top sheave and part of the support bracket from the mast of the WK270 CIS installation had fallen from the masthead into the cellar. The components that have come loose have fallen approximately 8 meters and landed in the WK 270 well cellar, no one was injured in this incident but given that the assembly that fall has an approximate weight of 10kg there was the potential under a different set of circumstances (had someone been present at the time of a failure) for major injury.
2018 | 08-2018 | Generation | Employee | No injury | Fatality | Asset failure | On Wednesday morning following the gale force winds the during the evening / night of Tuesday, a fixed vertical ladder cage on the western side of the SPP cooling tower, was found to have broken off and was laying on the gravel beside the ladder. This ladder is primarily used as a secondary escape exit from the upper levels of the cooling tower. The ladder and cage are of composite fibreglass construction.
2018 | 09-2018 | Distribution | Contractor | No injury | Serious harm | Work at heights | Workers were conducting pole change out process and were observed by an Aurora observer not employing a 100% restraint while working at heights.
|  | Distribution | Employee | No injury | Serious harm | Asset failure | On the 13/08/17 a power pole failed at Alexandria at approx. 18.50 hrs. The fallen pole resulted in fence damage and power lines across the roof of a residence. No injuries and minor damage to structures.
2018 | 09-2018 | Distribution | Contractor | No injury | Serious harm | Work at heights | Contractor observed displaying at risk behaviour while working at heights
2018 | 10-2018 | Distribution | Contractor | No injury | Serious harm | Electricity | Were following LV Cable and uncovering with shovel, checking no danger - services, cables, gas etc. Uncovered and exposed LV joint. One final scoop to clear fill and digger hit 11kV cable.
|  | Distribution | Employee | No injury | Serious harm | Asset failure | Wednesday 20th September 2017 we received reports of a power pole down outside 34 Stewart Street, Frankton, Queenstown.
2018 | 11-2018 | Distribution | Contractor | No injury | Serious harm | Work at heights | Contractor observed displaying at risk behaviour working at heights
|  | Distribution | Contractor | No injury | Serious harm | Electricity | At approx 12:36 28/9/17 A 3 Rd Party contractor working in Cromwell uncovered and made contact with a 6.6kv underground cable.
|  | Distribution | Employee | No injury | Serious harm | Asset failure | Pole failed at Chicago Street, Alexandra. The pole did not fail to ground. The pole was suspended by the HV and LV conductors. The pole failed at ground level.
2018 | 12-2018 | Distribution | Contractor | No injury | Serious harm | Electricity | Contractor carrying out work outside IHC transformer around 287 Middleton Rd and hit the Corstorphine 2 feeder. They were digging a hole to install a LV link box outside the transformer substation site, however they stuck the C02 feeder cable and caused it to fail.
2018 | 13-2018 | Distribution | Contractor | Serious harm | Serious harm | Mobile powered plant | Tree Work Clearing Private pine plantation away from East Tairei 3 line for Aurora. Digger pushed over a hanging tree which fell between a number of stumps. When the digger moved the tree it created tension breaking the tree and sending a large splinter flying which struck one of our arborists in the left side of his head. He was taken to Hospital as a precaution.
2018 | 14-2018 | Distribution | Contractor | No injury | Serious harm | Mobile powered plant | Contractor observed at risk working under a suspended load
2018 | 15-2018 | Distribution | Contractor | No injury | Serious harm | Mobile powered plant | Contractors placing themselves in the line of fire when standing in the swing arc of an excavator.
|  | Distribution | Contractor | No injury | Serious harm | Electricity | A 3rd Party Electrician working on a damaged service cable on a property was exposed to an electric shock risk when fuses were livened by a Delta fault crew while he was working on the damaged cable
|  | Distribution | Contractor | No injury | Serious harm | Electricity | Work crew incorrectly installed generator leads to overhead lines and reversed the polarity, which resulted in damage to appliances in the residence.
|  | Distribution | Contractor | No injury | Serious harm | Electricity | Work crew incorrectly reversed the polarity in a residence causing damage to internal appliances.
2018 | 16-2018 | Generation | Employee | No injury | Serious harm | Lone working | During June, a Meridian Door to Door employee entered a property and was assaulted by the resident of the property when he pushed and kissed her. The employee was not hurt but very shaken by the event.
2018 | 17-2018 | Generation | Contractor | No injury | Serious harm | Electricity | A contractor Balance of Plant Operator accessed a low voltage kiosk while energised to carry out an inspection. The signage on the kiosk clearly stated that the Transformer should be de-energised and earthed before opening due to risk of arc flash.
2018 | 18-2018 | Generation | Employee | No injury | Fatality | Work at heights | A hub hatch was found on the ground. The hatch was not engaged fully into the hole and was not double checked after it was closed.
2018 | 19-2018 | Generation | Employee | No injury | Serious harm | Work at heights | An employee descended and ascended a turbine without a harness and no means of communication.
2018 | 20-2018 | Distribution | Employee | No injury | Serious harm | Electricity | Near miss involving the foreman attempting to hand back an access permit to control room that all men were clear of the line and it was clear to liven. Other crew was still working on spur line and overheard conversation on RT. Contacted control room and foreman to notify that they were still working on the line
2018 | 21-2018 | Distribution | Employee | No injury | Serious harm | Driving | uncontrolled movement of truck
2018 | 22-2018 | Distribution | Employee | No injury | Serious harm | Work at heights | Fall from EWP
2018 | 23 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Cable drum crashed from Jinker whilst being winched on
2018 | 24 | Distribution | Employee | No injury | Serious harm | Electricity | RMU operated remotely while a field operative was accessing it
2018 | 25 | Distribution | Employee | No injury | Serious harm | Driving | Boom of crane got stuck under low bridge
2018 | 26 | Distribution | Employee | Minor injury | Serious harm | Work at heights | side rail of ladder fractured while employee was decending. Employee fell to ground
2018 | 27 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Whilst tensioning conductor the line broke hitting the employee on both hand and face
2018 | 28 | Distribution | Employee | Minor injury | Serious harm | Asset failure | cracked Insulator broke and a piece fell on employees head while wearing his hard hat
2018 | 29 | Distribution | Employee | No injury | Serious harm | Asset failure | Conductor broke and fell to the ground
2018 | 30 | Distribution | Employee | No injury | Serious harm | Driving | Tailgate fell of trailer while driving
2018 | 31 | Distribution | Employee | No injury | Serious harm | Electricity | During pre-livening checks of a new metering unit, someone had changed the CB relay settings to a different setting from thoswe specified by the engineer
2018 | 32 | Distribution | Employee | No injury | Serious harm | Work at heights | Ladder failed
2018 | 33 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Ladder was blown off the pole by the wind before it had been tied down
2018 | 34 | Distribution | Employee | No injury | Serious harm | Electricity | Gas switch closed in error
2018 | 35 | Distribution | Employee | No injury | Serious harm | Electricity | Hit an unidentified service whilst driving an earth pin intot he ground
2018 | 36 | Distribution | Employee | Serious harm | Serious harm | Hazardous materials | Slipped on substance on floor whilst carrying cable drum on arm, fracturing arm
2018 | 37 | Distribution | Employee | No injury | Fatality | Electricity | Tree "barbers chair" split whilst being felled causing it to fall in an unitended direction, hitting and breaking live 11kV powerline causing loss of power to customers
2018 | 38 | Distribution | Employee | No injury | Fatality | Electricity | Pillar box found smoking and fizzing when worker when to replace it after being hit by car. On closer inspection wires inside found to be wrapped in tape that may contain metal.
2018 | 39 | Distribution | Employee | No injury | Serious harm | Lone working | Call centre received threatening phone calls from customer on fault line who had no power. Faultman could have been at risk if threats had been real had they attended property to investigate unaccompanied. Went escorted by police
2018 | 40 | Distribution | Employee | No injury | Fatality | Electricity | Arc cutting jumper
2018 | 41 | Distribution | Employee | No injury | Serious harm | Electricity | Attending fault at SP2188. Opened Pillar to assess fault and lost control of pliers that dropped onto live connections causing a phase to phase flash over. Worker was distracted by co-worker who was talking and lost concentration momentarily at a critical stage of the process. Worker returned to work the following day on light duties. As a result of this incident all live work was suspended, which eliminates the risk of re-occurrence of this incident. A separate work stream has been established to consider the subject of future live work including procedures etc. This is incident was reportable to WorkSafe NZ as they consider a "flash over" to be the same as electrocution. They have advised that they will take no further action on this incident.
2018 | 42 | Distribution | Contractor | No injury | Serious harm | Electricity | Employee called to construction site where security guard and another third party received an electric shock from a fence at Victoria Square. They were not injured. The fault was found to be due to a neutral not connected to the bus bar in a distribution box. We notified Worksafe of the event and they elected not to investigate further.
2018 | 43 | Distribution | Employee | Minor injury | Serious harm | Work at heights | Employee fell from ladder sustaining fractures and other injuries. Worksafe was notified, and did not investigate further.
2018 | 44 | Distribution | Contractor | Minor injury | Serious harm | Electricity | When undertaking circuit breaker pressure testing on the Orion equipment, a contractor employee came into contact with the live test lead from which he received an electric shock. The subsequent injury developed overtime into a lost time injury.
2018 | 45 | Distribution | Contractor | Minor injury | Serious harm | Not listed (specify in narrative) | A contractor employee cut the underside soft tissue of his thumb while stripping a cable. Worksafe has closed the file and is not investigating further.
2018 | 46 | Distribution | Contractor | No injury | Fatality | Driving | 2 crew stranded in vehicle driven into flooded river at night during storm event. Swam to safety.
2018 | 47 | Distribution | Contractor | No injury | Fatality | Electricity | 11kV line under works contacted live 33kV Line. Potential for Multiple fatalaties.
2018 | 48 | Distribution | Contractor | No injury | Serious harm | Asset failure | Low HV Line across road, low enough for truck to pull down. Post recent works.
2018 | 49 | Distribution | Employee | Serious harm | Fatality | Driving | Reversing down a farm track and truck rolled down a bank. Whilst rolling an employee's tip of his finger was severed. Truck was submerged in river.
2018 | 50 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | Whilst working under a building stretched to complete a task and hurt shoulder.
2018 | 51 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | While working up pole reached out to use come along and strained back.
2018 | 52 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | Line mechanic unbounding conductor from fallen pole dislocated right shoulder and strained left shoulder when trying to raise the wire in the air.
2018 | 53 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | Line mechanic injured shoulder while manually pulling overhead conductor.
2018 | 54 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | Utility arborist injured shoulder while cutting and holding branches.
2018 | 55 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | Storeman rearranging fish bins of square washers on pallet. Felt lower abdominal strain and tightness.
2018 | 56 | Distribution | Employee | No injury | Fatality | Electricity | Utility worker attempted to cut through a live low voltage (240 volt) single core 16mm² copper neutral screened house service cable.
2018 | 57 | Distribution | Employee | No injury | Fatality | Electricity | Trainee cable jointer received minor electric shock between bare right hand and exposed right elbow, while stripping outer sheath on disconnected LV mains cable for testing purposes.
2018 | 58 | Distribution | Contractor | No injury | Fatality | Electricity | AP Issued with HV isolations and no earths
2018 | 59 | Distribution | Public Safety | No injury | Serious harm | Electricity | Member of the public interfering with a stay wire
2018 | 60 | Distribution | Contractor | Production Loss (minor) | Fatality | Asset failure | Pole incorectly installed (Worksite shut down)
2018 | 61 | Distribution | Employee | No injury | Operational (Major) | Lone working | Redundancy issue for on call staff who are unwell
2018 | 62 | Distribution | Contractor | Production Loss (minor) | Production Loss (major) | Electricity | A parallel was made between 33kV Feeders and the ARs in line with these feeders did not have the Earth Fault Pickup disabled by the controller
2018 | 63 | Distribution | Public Safety | No injury | Serious harm | Electricity | Safety Concern from member of public - UG box lid left open and wires exposed
2018 | 64 | Distribution | Contractor | No injury | Fatality | Electricity | Contractor working on network without a permit
2018 | 65 | Distribution | Contractor | No injury | Serious harm | Not listed (specify in narrative) | Result of a splinter that had become infected, the injury required two doctor visits for cleaning and removing the splinter.
2018 | 66 | Distribution | Contractor | Minor injury | Serious harm | Not listed (specify in narrative) | This medical treatment injury involved a contusion / haematoma that was initially reported as pain/discomfort but pain continued and a MRI was required.
2018 | 67 | Distribution | Contractor | Minor injury | Serious harm | Work-related ill-health | Contractor suffered a neck strain which required frequent doctor visits. A reminder to all contractors of their contractual requirements was sent out.
2018 | 68 | Distribution | Contractor | Minor injury | Serious harm | Work-related ill-health | A subcontractor reported tht he had strained his lower back while moving fence barriers on a residential external connection.
2018 | 69 | Distribution | Employee | Minor injury | Serious harm | Work-related ill-health | An employee sprained his back while carrying a drum of cable in the yard. The employee had to undergo short series of osteo treatment.
2018 | 70 | Distribution | Contractor | Minor injury | Serious harm | Not listed (specify in narrative) | A contractor was alighting from the back of a crane truck. He tripped and fell forward hitting his knee on a concrete pole.
2018 | 71 | Distribution | Contractor | Minor injury | Serious harm | Work-related ill-health | A contractor twisted his lower back while dragging branches to the chipper.
2018 | 72 | Distribution | Contractor | Minor injury | Serious harm | Work-related ill-health | A contractor was carrying his ladder when a gust of wind caught the ladder and caused his to twist his shoulder.
2018 | 73 | Distribution | Employee | Minor injury | Fatality | Driving | Staff member leaving driveway to attend a fault and has contacted with cyclist. Cyclist taken to A & E for an x/ray resulting in a fracture to th eright arm / wrist.
2018 | 74 | Distribution | Employee | Serious harm | Serious harm | Not listed (specify in narrative) | Straining up conductor and started pulling when a join in the conductor failed causing conductor to snap and comealong thrown back towards worker
2018 | 75 | Distribution | Employee | No injury | Fatality | Electricity | Two crews straightening a pole transformer, TMP in place and monitored by Traffic Management Services. Stock Truck (unsure of transport company at this time) came through and clipped wire. Both truck driver and crews checked to establish no injuries.
2018 | 76 | Distribution | Employee | No injury | Fatality | Not listed (specify in narrative) | While attending a fault at 84 West Plains Rd, Invercargill and proceeding to cross the bridge to gain access to the network, the bridge gave way under the EWP, stranding the vehicle on the bridge. (no signs were at bridge or along road to indicate the bridge could not be driven on) Vehicle: KCB148
2018 | 77 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Certain Reyrolle switch gear have an Operating Restriction placed on them that say they can only be operated with the complete RMU de-energised. RMU 824 Rockdale Rd Nth of Tweed has this operating restriction. SW 2 Earth Switch was closed with the RMU alive. Isolation was being provided for a cable fault.
2018 | 78 | Distribution | Employee | No injury | Serious harm | Asset failure | Opened Clapham ABS HV vertical switch Porcelain Insulator fell from ABS onto left foot just missing shoulder on its decent
2018 | 79 | Distribution | Contractor | No injury | Fatality | Electricity | As part of a job to supply power to a new Car Charger at Pak'N'Save Frankton, a pillar box was to be installed and connected into a spare de-engerised 400V link cable. Three of the cables feed out of the transformer were exposed and one of them was identified as the de-energised cable. It was spiked and cut through on one side (At this stage there was no indication the cable was live) they started to cut the other side of the cable when there was a flash.
2018 | 80 | Distribution | Contractor | No injury | Fatality | Electricity | Contractor putting in Telco pole, with in 4m Mads, Plant also not bounded, no safety observer or work authority. Discussed with Contractor, the correct procedure and requirements for working within the Mads, site was shut down further action to be sorted out with PNL staff.
2018 | 81 | Distribution | Employee | No injury | Fatality | Electricity | TLC employee cut through an underground cable, without positively identification, assumption was it was redundant, turned out to be an in-service communication cable however it could have been a single leg paper lead cable.
| 82 | Distribution | Third party | No injury | Fatality | Electricity | Unauthorised access into our LV pillar by unknown third party
2018 | 83 | Distribution | Employee | No injury | Serious harm | Lone working | Verbal treat to staff member treat of shooting
2018 | 84 | Distribution | Employee | No injury | Fatality | Driving | Loss of ladder on to road from moving vehicle during transit
2018 | 85 | Distribution | Employee | No injury | Serious harm | Work at heights | Falling object from pole stuck employee on leg (spanner)
2018 | 86 | Distribution | Employee | No injury | Fatality | Driving | Employee identified damage to ladder rack prior to driving, ladder could have had the potential to come free from moving vehicle had this not been identified
2018 | 87 | Distribution | Employee | No injury | Fatality | Asset failure | Employees were removing an old pole during removal the pole broke at ground level causing the pole to fall to the side, the employees has set up an exclusion zone for this and no employees were in the zone.
2018 | 88 | Distribution | Employee | No injury | Serious harm | Plant and equipment | Identified guarding bypassed on bench mounted grinder
2018 | 89 | Distribution | Employee | No injury | Fatality | Driving | Trailer pin came free whilst driving on gravel road
2018 | 90 | Distribution | Contractor | No injury | Fatality | Electricity | Tree workers made inadvertent contact with LV overhead conductors causing tripping
2018 | 91 | Distribution | Employee | No injury | Fatality | Electricity | Arc-flash caused due to incorrect operation HV equipment
2018 | 92 | Distribution | Contractor | No injury | Fatality | Mobile powered plant | Contractor was undertaking pole replacement in conjunction with TLC utilizing an excavator during this process the operator swung the excavator around making contact with an old pole causing the pole to fail
2018 | 93 | Distribution | Employee | No injury | Serious harm | Asset failure | Insulator broke during operation of ABS hitting employee no injury
2018 | 94 | Distribution | Employee | No injury | Fatality | Driving | Loss of control of vehicle
| 95 | Distribution | Employee | No injury | Fatality | Driving | Reversed into mobility scooter
| 96 | Distribution | Employee | No injury | Fatality | Driving | Ladder not secured to vehicle
2018 | 97 | Generation | Employee | No injury | Fatality | Not listed (specify in narrative) | Sored energy/Work Control Procedures - Worker went to work on wrong side of isolation, stopped by another member of the work party
2018 | 98 | Generation | Employee | No injury | Fatality | Electricity | Refilling of 110/11 kv transformer whilst energised without correct work control procedures in place.
2018 | 99 | Distribution | Employee | Serious harm | Serious harm | Not listed (specify in narrative) | Hit on head by tree limb resulting in concussion - reported to Worksafe (vegetation worker - not listed in critcal risk)
2019 | 01-2019 | Distribution | Contractor | Serious harm | Serious harm | Hazardous materials | Non Electrical - A large rock was to be placed in the garden outside Alpine House, so that a plaque could be fixed to it to mark the formal opening of the building. The rock has to be lifted into the approximare location. While manoeuvring the rock into the best orintation, the lifting strops caught the involved persons hand. The involved person requested the rock be lowered right away. Once the strops had been realeased the nature of the injury was clear partical de gloving and a crush injury to the persons finger.
2019 | 02-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Near miss involving a member of staff attending a fault, he noticed a spark on the cross-arm and as he climbed the ladder with his LV gloves on he tested the the cross-arm and as he climbed the ladder with his LV gloves on he tested the cross-arm and found it was live
2019 | 03-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Near miss involving a worker at a fault situation and had one blown HV fuse. He noticed earth lead had come off earth pin and assumed this was the issue. He noticed earth lead had come off earth pin and assumed this was the issue. He opened the other HV fuses at the Tx, fixed the earth lead and closed in the HV fuses. As he did he noticed sparking at the mains entry point at the house. So he pulled the HV fuses straight away and tagged to get mains entry fixed ASAP.
2019 | 04-2019 | Generation | Employee | No injury | Serious harm | Asset failure | Wairakei G7 Left Hand Emergency Stop Valve (ESV) hung up momentarily on shut down. Valve was retested on start-up and failed to move. Start-up halted and remediation work undertaken on valve. Stand-back engineering review of LP machine ESVs being undertaken.
2019 | 05-2019 | Generation | Employee | No injury | Serious harm | Asset failure | G10 Right Hand Emergency Stop Valve did not close when the machine tripped. ESV hung up. Was repeatedly manually tripped by the operators but was stuck in the open position. Valve maintained and unit returned to service.Critical Safety Device Failure
2019 | 06-2019 | Generation | Employee | No injury | Fatality | Work at heights | During rig up for a fishing operation on a geothermal well, an operator placed an 8kg part of the fishing tool on the scaffold around the well head. While the operator descended from the access ladder to the scaffold, the tool rolled off the scaffold platform and dropped approximately 3 meters and hit the slickline sheave at ground level. It was found that despite the kick board had not been installed (where the tool fell) & other safety issues, the scaffold had been incorrectly signed off as safe.
2019 | 07-2019 | Generation | Employee | No injury | Serious harm | Not listed (specify in narrative) | K-line steam piping was found to have a section flooded with cold condensate water as a result of a blocked drain. The cold water poses a significant risk of causing of severe pressure collapse and in and failure of the pipeline if it comes into contact and condenses steam in the line. Access to area restricted and system was held in steady state. Work was slowly undertaken to warm and remove the water without altering the interface between steam and water. Plant needed to operate outside its design conditions during this process.
2019 | 08-2019 | Generation | Contractor | No injury | Serious harm | Hazardous materials | Contractors were engaged to carry out remedial works on a geothermal bleedline. During this work they carried out work outside of the permit when they used a disc grinder to cut into a pressurised gas line which led to H2S gas being released.
2019 | 09-2019 | Distribution | Employee | Minor injury | Fatality | Traffic management | OHL worker within defined traffic management area was struck by member of the public who was on his phone while driving through a restricted speed area.
2019 | 10-2019 | Distribution | Employee | Minor injury | Serious harm | Mobile powered plant | Civil worker was struck a glancing blow by a mini excavator while it was trafficking through the work site
2019 | 11-2019 | Distribution | Employee | Minor injury | Serious harm | Mobile powered plant | Installation of cable hauling rope into cable ducts. A superceded installation practice was being utilised by an inexperienced worker. The workers hand was injured and a minor fracture to the wrist was sustained. The worker was wearing gloves.
2019 | 12-2019 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | While restringing an overhead line repair one of the clamps holding the line slipped and narrowly missed the linesmans face
2019 | 13-2019 | Distribution | Employee | No injury | Fatality | Not listed (specify in narrative) | Two faultman working at night were threatened by the tenant with a knife.
2019 | 14-2019 | Distribution | Contractor | Minor injury | Fatality | Driving | Contractor fell asleep at the wheel while driving to work and left the road and crashed.
2019 | 15-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Cable jointing tooling slipped while carryining out jointing operations.Cut to hand. Stiches required
2019 | 16-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Contractor carrying out directional drilling hits HV underground cable
2019 | 17-2019 | Distribution | Employee | No injury | Fatality | Electricity | Incorrect switching procedures
2019 | 18-2019 | Distribution | Employee | No injury | Fatality | Electricity | Earthing transformer closed on earthing pin that was innadvertantly left in place following commissioning tests
2019 | 19-2019 | Distribution | Employee | No injury | Fatality | Electricity | LV lines found to be still energised during works
2019 | 20-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Auger to install new pole hits LV service cable.
2019 | 21-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Contractor carrying out directional drilling hits LV underground cable
2019 | 22-2019 | Distribution | Employee | No injury | Fatality | Driving | There have been a number of trailer related incidents. Usually the trailer detaches from the towing ball and is caught by the breakaway chains.
2019 | 23-2019 | Distribution | Employee | Serious harm | Serious harm | Work-related ill-health | This event is unusual, in that it was not a serious event but led to a serious infection (cellulitis). Essentially our worker bumped his leg against a door sill while getting in, and that bump turned into cellulitis. There was no critical risk involved, no activity that was preventable as such, and the opportunities for learning were only around early diagnosis through monitoring of an injury.
2019 | 24-2019 | Distribution | Employee | Serious harm | Serious harm | Not listed (specify in narrative) | worker sufferred a crush injury to their finger tip, resulting in the loss of finger tip, whill working on a pneumatic tool. The worker attempted to change the tool head while the tool was connected to air line. The tool has activiated as they leant over it crushing their finger tip.
2019 | 25-2019 | Distribution | Employee | Serious harm | Serious harm | Falls | Slilpped on uneven ground in riverbed, outstretched hand to break fall which resulted in a fractured schapoid bone in the wrist. This was a university student on an internship.
2019 | 26-2019 | Distribution | Employee | No injury | Fatality | Driving | Sunstrike whilst driving nearly caused a collision.
2019 | 27-2019 | Distribution | Employee | No injury | Fatality | Driving | Other speeding vehicle nearly caused a motor vehicle accident.
2019 | 28-2019 | Distribution | Employee | No injury | Serious harm | Driving | Almost hit from behind by a vehicle in an 80 kph zone whilst waiting to turn right into work
2019 | 29-2019 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Foot slipped when getting out of vehicle
2019 | 30-2019 | Distribution | Employee | No injury | Serious harm | Driving | Truck and trailer mergeting in 100 kph zone almost collided with workers vehicle. Evasive action taken.
2019 | 31-2019 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Stepped into a streetlight hole and sunk up to mid-thigh.
2019 | 32-2019 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Walking towards door which was flung open, very close to being struck with force by the door.
2019 | 33-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Crushed finger while stacking materials against headboard on truck
2019 | 34-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Tripped on a slab in the long grass and landed on back and arm.
2019 | 35-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Slipped on a rock and hit knee and shoulder
2019 | 36-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Arcing incident from solenoid contacting generator on vehicle.
2019 | 37-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Arcing incident from tree blowing into lines
2019 | 38-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Carrying a pole which caught on something and flicked around and contacted front tooth.
2019 | 39-2019 | Distribution | Employee | No injury | Serious harm | Driving | Had to take evasive action when a car continued on straight whilst indicating to turn right on the open road.
2019 | 40-2019 | Distribution | Employee | No injury | Serious harm | Not listed (specify in narrative) | Small fire started on top of truck gearbox
2019 | 41-2019 | Generation | Employee | No injury | Fatality | Hazardous materials | Rotokawa geothermal - pentane leak while replacing mechanical seal
2019 | 42-2019 | Generation | Employee | Minor injury | Fatality | Driving | Road - Vehicle forced off road by oncoming public vehicle
2019 | 43-2019 | Generation | Employee | No injury | Fatality | Driving | Road - Had to take evasive action to avoid oncoming public vehicle
2019 | 44-2019 | Generation | Contractor | No injury | Fatality | Hazardous materials | Mokai geothermal - Pentane spill to ground when RASM not applied
2019 | 45-2019 | Generation | Employee | No injury | Fatality | Electricity | Ngatamariki geothermal - Incorrect identification of lube oil fan to be worked on
2019 | 46-2019 | Generation | Employee | No injury | Fatality | Asset failure | a turbine had a low speed lock in place preparing for a gearbox removal early the week after. The following week, technicians found rotor bolts in the ground, on the hardstand and surrounding paddock. The rotor lock failed in wind speeds above 13m/s over the weekend.
2019 | 47-2019 | Generation | Employee | No injury | Fatality | Work at heights | During height training at Te Apiti a Petzal I'D descender opened as a trainee went over the edge of the Turbine. It is believed his back up device rubbed against the black swinging lock on the carabiner attachment allowing the swinging gold cheek/plate of the I'D to open. The trainee was brought back to the top of the turbine where his I’D was inspected and re-secured. During the second descent the I'D once again released. The trainee, with the support of the trainer, were able to lower him slowly to the ground.
2019 | 48-2019 | Generation | Employee | No injury | Serious harm | Work at heights | Walking on top of Unit 2 rotor under a Test Permit with a full penstock. Isolations were in place however do not prevent the rotor from turning as result of wicket gate leak.
2019 | 49-2019 | Generation | Contractor | Serious harm | Serious harm | Not listed (specify in narrative) | Rotating Plant Critical Risk. Contractor was moving across nacelle when he lost his footing and tripped, reaching out to brace himself the index finger of his left hand made contact with high speed brake disc. After being admitted to hospital it was confirmed the fingertip could not be reattached.
2019 | 50-2019 | Generation | Contractor | No injury | Fatality | Electricity | Work was being completed in a switchboard with live cables at Aviemore by a contractor. While a cable was being pushed through a hole it fell more quickly than anticipated and connected with a live conductor causing a flashover. The plant did not trip, protection did not operate and there was no injury.
2019 | 51-2019 | Generation | Contractor | No injury | Fatality | Driving | A scaffolding contractor was travelling to site to commence establishment of a project on a foggy morning. The driver lost sight of the road and when he applied the brakes (travelling at approx. 55km/h) the trailer he was towing came around causing the truck to hit the curb and rollover. The driver was shaken but unharmed. Fire brigade and Police attended the event.
2019 | 52-2019 | Generation | Contractor | Serious harm | Serious harm | Not listed (specify in narrative) | Contractor using a mechanical winch to hoist a tool bag. Fingers on the left hand became trapped in the winch mechanism causing lacerations and factures to multiple fingers.
2019 | 53-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Close-Call - While opening and then closing 11kV links 615, an unexpected long arc draw that nearly arced the entire length of the candle swing occurred. No flash over occurred.
2019 | 54-2019 | Distribution | Contractor | Minor injury | Serious harm | Driving | Staff member assaulted by member of the public in road rage incident
2019 | 55-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Contractor requested last min live line permit to fit cover up gears for him to complete a minor works permit for the day. NTL explained that he does not require this as under his MW he can carry out his MW while maintaining his MAD. NTL reiterated that if there was any doubt the he could not carry out his work by maintain his MAD or if there was a risk that something could occur where it meant that this was un achievable then he should not start work and that the line will need to be isolated, Earthed and he could carry out his work under a MW permit.
2019 | 56-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | When doing a fault, found a neutral connection to the next door property had not been connected when cable was livened.
2019 | 57-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Failed to take out permit for access electrical network and left electrical network in unsafe condition.
2019 | 58-2019 | Distribution | Contractor | Minor injury | Serious harm | Not listed (specify in narrative) | Arborists was struck by a falling tree branch.
2019 | 59-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Contractor on checking the approved permit for run 1 he noticed a difference in the permit to his application. Contractor went onto check run 2 and found differences as well. Kelly contacted control room and discussed the findings and agreed on new IE sites
2019 | 60-2019 | Distribution | Contractor | No injury | Fatality | Driving | Worker fell asleep causing loss of control of light vehicle
2019 | 61-2019 | Distribution | Employee | No injury | Fatality | Not listed (specify in narrative) | Dropped/Nil phone audio during fault calls
2019 | 62-2019 | Distribution | Employee | No injury | Serious harm | Asset failure | Gas bottle hose failed
2019 | 63-2019 | Distribution | Employee | No injury | Serious harm | Asset failure | Head of pole broke
2019 | 64-2019 | Distribution | Employee | No injury | Serious harm | Mobile powered plant | Pallets fell off forklift
2019 | 65-2019 | Distribution | Employee | No injury | Fatality | Electricity | Legally Priviledged
2019 | 66-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Control not informed that issuer earths had been applied
2019 | 67-2019 | Distribution | Employee | No injury | Serious harm | Work at heights | Potential to fall from height due to unsafe behaviours
2019 | 68-2019 | Distribution | Employee | No injury | Fatality | Electricity | Contact with electricity resulting in electric shock (no injury) when replacing a fuse and fuse base in a boundary box.
2019 | 69-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Contractor breached MAD when cable jointing.
2019 | 70-2019 | Distribution | Contractor | Minor injury | Fatality | Electricity | Contractor recevied electric shock while carrying out commissioning checks on a circuit breaker.
2019 | 71-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Contractor cut into live 11kV Cable, believing they were cutting into a low voltage cable. Serious near miss.
2019 | 72-2019 | Generation | Contractor | Serious harm | Serious harm | Not listed (specify in narrative) | No critical risk was involved. Contractor rolled his ankle on flat solid ground (with a little shingle on it). Both contractors were returning to the vehicle along the edge of the grass. Robert suddenly fell to the ground in moderate pain. It is suspected Robert slipped on small stones that rolled under his foot on the hard dry ground. Ian remarked he heard a crack as Robert fell. Robert was unable to move; his leg was not weight bearing. Tim Hope, the Orchard Manager for El Pedegru Orchard arrive. Ian called for an ambulance and proceeded to the intersection of Fraser Road and Stroad Road to meet the ambulance and escort them to Robert. Tim stayed with Robert until the ambulance arrived. Went in for surgery yesterday (25 March). Fitted plates to both the fibula and tibia just above the ankle. The third bone fracture is expected to heal naturally. Relocated ankle as it had dislocated and removed a bone fragment. All good! Initially I thought my knee failed first however, in hindsight and after discussing with surgeons the force exerted on the ankle with a dislocated knee would be insufficient to fracture the ankle so dramatically. The foot slipping sideways would have fractured and dislocated the ankle followed by the knee not supporting the weight of me falling, hence the patella dislocating as a secondary injury.
2019 | 73-2019 | Distribution | Contractor | No injury | Fatality | Driving | Driver fell asleep at wheel, drifted onto the grass left hand verge.
2019 | 74-2019 | Distribution | Contractor | No injury | Fatality | Driving | ATVU lost traction on descent. Driver & passenger abandoned ATVU which left track and rolled down hill.
2019 | 75-2019 | Distribution | Contractor | No injury | Fatality | Mobile powered plant | Truck winch used for task not intended to use for. Truck rolled forward over chocks and down hill striking another vehicle. Secondary vehicle has rolled down embankment coming to rest next to residential property.
2019 | 76-2019 | Distribution | Contractor | No injury | Fatality | Driving | Driver failed to adequately check the road was clear prior to making the u turn manoeuvre resulting in a collision with an oncoming vehicle
2019 | 77-2019 | Distribution | Employee | No injury | Fatality | Driving | MOP collided with employee in 100km/h zone. Employee not at fault.
2019 | 78-2019 | Distribution | Contractor | No injury | Fatality | Driving | Ute with tandem trailer lost traction and slid over bank landing on SH below property.
2019 | 79-2019 | Distribution | Employee | No injury | Fatality | Electricity | No spotter, barrier or safety process was in place to make employee aware or prevent him from touching the open end of the cable.
2019 | 80-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Near Hit / Incorrect installation of drop out HV fuse carriers
2019 | 81-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Left knee hit by chain - attempting to pull the chain out from an old pole and the chain came out and hit my left knee.
2019 | 82-2019 | Distribution | Employee | Serious harm | Fatality | Electricity | LV Arc Flash
2019 | 83-2019 | Distribution | Employee | No injury | Fatality | Driving | Employee Using Cellphone while Driving PowerNet Vehicle
2019 | 84-2019 | Distribution | Employee | No injury | Fatality | Driving | Vehicle Loss of Control
2019 | 85-2019 | Distribution | Employee | No injury | Fatality | Driving | Work truck vs fence - lost control and drove down the bank and through the farmers fence.
2019 | 86-2019 | Distribution | Employee | No injury | Serious harm | Electricity | Shallow Power Cables
2019 | 87-2019 | Distribution | Employee | Minor injury | Fatality | Driving | Work vehicle roll over
2019 | 88-2019 | Distribution | Employee | No injury | Fatality | Electricity | Potential livening of 11kV cables that disconnected and the ends cut
2019 | 89-2019 | Distribution | Employee | No injury | Serious harm | Lone working | Aggressive customer grabbed and threatened an employee, whilst caring out work in isolation
2019 | 90-2019 | Distribution | Employee | Minor injury | Fatality | Electricity | Shorting of LV cables in TX resulted in Arc-Flash, employee was working in close proximity to Live LV
2019 | 91-2019 | Distribution | Employee | No injury | Serious harm | Driving | Ladder not secured on vehicle, ladder detached during driving falling on to the road.
2019 | 92-2019 | Distribution | Employee | Minor injury | Serious harm | Work at heights | Loss of control of conductor during pole change, employee dislocated shoulder
2019 | 93-2019 | Distribution | Employee | No injury | Fatality | Driving | Loss of control of vehicle resulting in a crash, distraction was the cause.
2019 | 94-2019 | Distribution | Contractor | No injury | Fatality | Work at heights | Ladder on scaffold site not installed correctly, ladder moved when worker was ascending, there was no fall.
2019 | 95-2019 | Distribution | Employee | No injury | Serious harm | Driving | Loss of control of line truck when 4wding, descending steep track. Truck slid off track and came to rest against a tree.
2019 | 96-2019 | Distribution | Employee | Minor injury | Serious harm | Not listed (specify in narrative) | Employee fell tripped and fell down stairs.
2019 | 97-2019 | Distribution | Employee | No injury | Serious harm | Work at heights | Conductor gave way when line guard was removed, could have resulted in injury due to falling objects.
2019 | 98-2019 | Distribution | Employee | No injury | Serious harm | Hazardous materials | Work process not followed when removing meters from potential ACM boards.
2019 | 99-2019 | Distribution | Employee | No injury | Fatality | Traffic management | Dropped conductor onto State Highway
2019 | 100-2019 | Distribution | Employee | No injury | Serious harm | Asset failure | Pillar Fire Haruru - proximity to hazardous substances
2019 | 101-2019 | Distribution | Contractor | No injury | Serious harm | Mobile powered plant | Reversed controls on MEWP
2019 | 102-2019 | Transmission | Contractor | No injury | Serious harm | Driving | A ute undertaking a U-turn on the open road was struck by a following vehicle. Fortunately, nobody was hurt, but people in both vehicles could have been seriously hurt.
2019 | 103-2019 | Transmission | Contractor | Minor injury | Fatality | Not listed (specify in narrative) | Helicopter dropped one skid on a steep ridge to unload line maintenance gear. A strong tail wind gust occurred at the same time the crew member re-boarded the empty helicopter, unbalancing it. The pilot immediately lifted off, with the toe of the skid catching and breaking two high tensile wires in the nearby stock fence. The helicopter flew towards two linemen on the ground, who took evasive action. One of the lineman fell and strained his back in the process, but fortunately was not seriously injured.
2019 | 104-2019 | Transmission | Employee | No injury | Serious harm | Driving | A near miss occurred when driving between Twizel & Waitaki (Sailor Cutting). An oncoming car crossed the centre line on a curve, turning into a roadside observation area overlooking Lake Benmore. The Transpower driver had to take evasive action to avoid a head-on collision
2019 | 105-2019 | Transmission | Contractor | No injury | Serious harm | Not listed (specify in narrative) | A subcontractor at the Kawerau substation was attempting to move a redundant 20 tonne transformer using a traverser trolley. There was an uncontrolled movement of the transformer which caused the trolley to move away and resulted in the transformer partially tipping over. No one was injured, however there was one person nearby at the time of the incident. Early indications are that planning and change management were key factors in this incident.
2019 | 106-2019 | Transmission | Contractor | No injury | Serious harm | Electricity | A hiab was unloading a portacom from a truck at an Auckland commercial site below overhead 220kV lines. During the lift the hiab came into close contact with a conductor, resulting in a flashover and tripping of the circuit. Fortunately, the operator was not injured, and the hiab suffered no significant damage.
2019 | 107-2019 | Transmission | Contractor | No injury | Serious harm | Electricity | While walking across the switchyard Electrix’s lead technician observed a Delta linesman preparing to remove an earth from the Aurora take off area. He commented to the worker that it was part of his Assurance from Aurora, the linesman had been requested to take down the earth by the Aurora control room. The earth removal was stopped under the technicians’ instruction before any earths were removed, the Aurora control room was contacted and the work officially stopped.
2019 | 108-2019 | Transmission | Contractor | No injury | Serious harm | Electricity | While preparing for a single span earthwire replacement pull, the old earthwire broke outside of both the primary and secondary rigging. The earthwire landed across the below 110kV HEN-MPE-A line which resulted in a fault on two circuits and a loss of supply.
2019 | 109-2019 | Transmission | Contractor | Serious harm | Serious harm | Not listed (specify in narrative) | A vegetation worker received a severe lacteration to his thumb after the chainsaw he was using contacted his other hand, causing the cut to his thumb. He has undergone an operation and is recovering.
2019 | 110-2019 | Transmission | Contractor | Minor injury | Serious harm | Electricity | A contractor was repositioning a cable from one MCCB to another. He moved an in-service cable back to create room for the cable migration and in doing so caused a flashover. The employee sustained a burn to his finger.
2019 | 111-2019 | Generation | Employee | No injury | Fatality | Driving | Driving north on SH1 Taupo bypass in clear fine weather at 95km/h. Noticed large cloud of localized geothermal fog covering slip road exit from SHI bypass to Broadlands road. Slowed down for fog then moved into exit lane once in fog cloud. Had to brake hard as other vehicle had stopped in lane. Slowed and stopped vehicle fine but car following behind was too close and locked up brakes to avoid hitting my vehicle (no collision).
2019 | 112-2019 | Generation | Contractor | No injury | Fatality | Electricity | During the removal of cables, an incorrect cable was identified and cut. The cable was potentially live as it was still connected at both ends from the control panel to generator governor Panel. The cable normally contains a 110VAC frequency loop. No electric shock was reported. Post cutting, the cable termination was removed from each end and put into terminal connectors for safety of others. Fuses have now been tested and found to have blown. The neutral screen had protected the person from receiving an electric shock.
2019 | 113-2019 | Generation | Contractor | Minor injury | Fatality | Electricity | Cover of panel in generator removed to rewire 24 volt DC terminals, when contractor brushed live AC terminals and received electric shock to hand.
2019 | 114-2019 | Generation | Employee | No injury | Fatality | Hazardous materials | Discovery of asbestos fibres in dust within basement of station - generator also circulates air from basement in to station.
2019 | 115-2019 | Generation | Employee | No injury | Fatality | Not listed (specify in narrative) | Small Scrub fire was started due to a welding spark whilst erecting webforage safety barriers. The fire sentry used a by 20litre fire extinguisher to extinguish the flames which burnt a 2m square area of dry grass within 10-15 seconds. Although the WSSP had been completed in the morning pre work commencing with the fire risk identified and mitigations in place, the weather conditions changed rapidly after lunch. Noth west wind increased which funnelled up the pennstock slope, drying the existing fuel source and making conditions borderline for the first aid fire fighting appliances present. Work should have stopped at this point and a reassessment undertaken. Although the first aid appliance managed to extinguish the fire, 30 seconds more and the fire would have been too big to manage.
2019 | 116-2019 | Generation | Contractor | No injury | Fatality | Mobile powered plant | Station overhead crane was out on Permit for major overhaul with no-go zone (Barriers) established below the crane. The lead contractor opened the station loading bay door to load vehicle, in doing so creating an opening in the work-zone barrier. Technician contractor entered restricted work zone.
2019 | 117-2019 | Generation | Contractor | No injury | Serious harm | Mobile powered plant | A new digger operator was transferring soil from up slope to a down slope location while the digger was positioned on uneven ground. As the machine swiveled to face down slope it became unstable and began to topple. The digger operator immediately dropped the digger bucket to prevent any further movement. However, the angled position of the digger meant it had one track unable to get traction. The digger operator tried to re-position the machine to firmer ground by using a combination of the remaining tractable track in conjunction with a dragging motion using the bucket and boom. The operator was asked to shut down the engine and exist the machine.
2019 | 118-2019 | Generation | Contractor | No injury | Serious harm | Driving | A Moxy operator was driving the articulated dump vehicle along a straight but highly cambered section of an access track when the rear wheels slid sideways on soft wet ground and then caught on hard surface. The sudden stop of the slide caused the Moxy to lurch to the left becoming unstable and flop onto its side. The load of roading gravel discharged from the box bed and onto the ground. There was no damage to equipment or injury to the operator (he was buckled into the seat harness).
2019 | 119-2019 | Generation | Contractor | No injury | Serious harm | Driving | ruck dropping off material, driver applied handbrake and got out of truck but truck started to move. Driver jumped back into truck and applied brake.
2019 | 120-2019 | Generation | Employee | No injury | Fatality | Driving | Employees were driving in each of their vehicles, entering access road to power station. The road is gravel so speed is restricted to 30km/ph when a speeding tanker came around a bend and forced one employees to drive into the water table ditch and the other to take evasive action.
2019 | 121-2019 | Generation | Contractor | No injury | Fatality | Driving | Contractor was using Trustpower vehicle and a trailer to drop off culvert pipes. The trailer coupling became dislodged but was equipped with two robust safety chains.
2019 | 122-2019 | Generation | Employee | No injury | Fatality | Driving | Driving home from work, had a couple of blinky eye periods earlier, but pushed on, then fell asleep and drove off the road about 4m before waking up. Hauled the truck back on to the road without looking, 4 wheel drift into the opposite lane then slowly corrected to the left lane. The car which was following came to see if I was OK when I had stopped.
2019 | 123-2019 | Distribution | Contractor | No injury | Serious harm | Hazardous materials | Gas Stike - Concrete cutter contacted 32mm gas pipe that had been instered into a steel pipe
2019 | 124-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Worker received 'tingle' across chest after a third party activated a generator during a 3 pole shutdown
2019 | 125-2019 | Distribution | Contractor | Minor injury | Serious harm | Hazardous materials | A pocket of gas escaped from a ped causing the detector to alarm and read above 100ppm. Worker inhaled some gas Worker was taken to the hospital for a precautionary checkup.
2019 | 126-2019 | Distribution | Contractor | No injury | Serious harm | Driving | Crew was reversing an All Terrain Vehicle (ATV), on a forest track, when the track subsided causing the ATV to tip 90 degrees on to its side.
2019 | 127-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Employee made contact with live cable in excavation
2019 | 128-2019 | Distribution | Contractor | No injury | Fatality | Electricity | New subdivision. LV cable laid previous day. Came out to fit a link pillar and discovered the cable was live. It should not have been connected yet.
2019 | 129-2019 | Distribution | Contractor | Minor injury | Serious harm | Electricity | PI was completing a demo of a service at Apirana Avenue, Glen Innes. PI isolated the service cable by removing the service fuses and then removed the service supply from the fuse carriers. So that this service does not get livened again by a third party, PI cut the service cables at ground level. PI had cut through three service cables successfully with the use of ratchet cutters and when cutting the forth cable he has somehow also cut through a live phase. This is when the incident happened and the injuries were sustained.
2019 | 130-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Poor communication protocols resulted in a live switch being earthed down.
2019 | 131-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Arrived on site to undertake compliance checks and observed PI completing a live breach joint without wearing the correct insulated LV gloves and using a LV buzzer for testing.
2019 | 132-2019 | Distribution | Contractor | Serious harm | Fatality | Not listed (specify in narrative) | A sub-contractor was performing work in a freestanding Andelect cabinet with a JW3 LV frame connected to a 300kVA transformer with exposed copper bus bar when an arc flash occurred. We would note this as critical risk of fire / explosion.
2019 | 133-2019 | Distribution | Contractor | Serious harm | Serious harm | Not listed (specify in narrative) | A high voltage oil switch failed during planned switching operations. The switches oil tank ruptured and caught fire. We would note this as critical risk of fire / explosion.
2019 | 134-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | During a No Power Fault reported by a homeowner, the responding Fault Person discovered incorrectly disconnected wiring in a pillar by others. A live feed existed into a temporary builders supply which had had the meter removed.
2019 | 135-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | During reactive switching, a live feeder was earthed, resulting in overhead lines failing.
2019 | 136-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | 3rd party contractor excavated under live transformer and supported with timber frame.
2019 | 137-2019 | Distribution | Contractor | No injury | Fatality | Electricity | 3rd party potholing for gas mains and almost struck 11kV lines.
2019 | 138-2019 | Distribution | Contractor | No injury | Serious harm | Not listed (specify in narrative) | While a line truck was travelling up a steep incline, two strapped concrete poles slipped from the back of the truck onto the road. We would note this as critical risk of fall from height (people and plant).
2019 | 139-2019 | Distribution | Contractor | Minor injury | Serious harm | Not listed (specify in narrative) | Job involved removing hazardous trees adjacent to HV powerlines using MEWP with traffic control. While trimming a large Pine tree MEWP operator was using a top-handled chainsaw to cut and hold branches before dropping them to ground for chipping. As operator was cutting one branch about 1 metre length with pine cones using chainsaw in left hand and holding branch with right hand the weight of the branch pulled his right hand in contact with the chainsaw causing a cut to his right thumb. Operator descended out of bucket, spoke his colleagues who dressed his wound and took him to medical centre where he received stitches. We would note this as critical risk of Struck by or striking and object.
2019 | 140-2019 | Distribution | Contractor | No injury | Serious harm | Driving | While driving MEWP and chipper the truck has veered off the roadside then driver managed to get back onto the road but the chipper has spun round, disconnected from the truck pintle, somersaulted and landed up in the roadside drain.
2019 | 141-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Piling machine for the Northern Motorway Improvements (NCI) struck the overhead line.
2019 | 142-2019 | Distribution | Contractor | No injury | Serious harm | Not listed (specify in narrative) | Transformer C-1391 erupted in flames engulfing the unit and overhead lines. We would note this as critical risk of fire / explosion.
2019 | 143-2019 | Distribution | Contractor | No injury | Serious harm | Not listed (specify in narrative) | Oil switchgear failed during re livening after planned maintenance. We would note this as critical risk of fire / explosion.
2019 | 144-2019 | Distribution | Contractor | No injury | Fatality | Electricity | 3rd party pulling fibre cable near 33kV cable. They had B4UDig Plans but had not requested a Standover as required for working near sub-transmission cables (detailed in the instructions with the B4UDig Plans) and not located, marked out or confirmed the location of the 33kV.
2019 | 145-2019 | Distribution | Contractor | No injury | Fatality | Not listed (specify in narrative) | Person from Moving machinery walked under a suspended load (30 ton transformer). We would note this as critical risk of fall from height (people and plant).
2019 | 146-2019 | Distribution | Contractor | No injury | Fatality | Electricity | Client requested a pit be relocated. After their request was not completed they took it upon themselves to move the live cable, also resulted in the earth pin being damaged.
2019 | 147-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | Notification by Electrix that crane operator fell asleep and slew crane into overhead 110Kv transmission lines, no visible damaged to overhead conductor or structure, line was isolated on the day of the incident.
2019 | 148-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | 3rd party had hit a live underground power cable with a digger.
2019 | 149-2019 | Distribution | Contractor | No injury | Serious harm | Driving | Connect 8 contractor ASCO were attempting to hitch a transporter trailer up to a 6 wheel tipper truck on a hill (the trailer had been dropped of earlier in the day) the trailer had some how started to roll backwards down the hill/road. The trailer carried on, damaged a parked vehicle. The trailer continued to travel down hill until it swerved to the other side of the road where it collided with a concrete LV power pole.
2019 | 150-2019 | Distribution | Contractor | No injury | Serious harm | Electricity | 3rd party removed a house without disconnecting the power, (demolition disconnect). When they removed the house this left live cables on site. Worksafe was notified of the hazard left at the site. This was reported as an unsafe work act by address only, contractor is not known. There is no follow up response from WorkSafe expected.
2019 | 151-2019 | Distribution | Employee | Minor injury | Serious harm | Work-related ill-health | Lineman suffered a tear to his achilles when descending a ladder - this doesn't fit with two of the criteria as it is not serious harm or involved a critical risk from list
2019 | 152-2019 | Distribution | Contractor | Minor injury | Serious harm | Work-related ill-health | Arborist suffered back strain when he slipped
2020 | 01-2020 | Distribution | Employee | Minor injury | Serious harm | Vehicle impacts | Accident involving a worker rolling a worktruck and receiving a cut to his head and brusing around his body - 13/12/2019
2020 | 02-2020 | Distribution | Employee | Minor injury | Serious harm | Personal safety and security breaches | Employee infringed crane safety distance when it was retracting stabalising legs. Employee placed his hand on the retracting leg and their fingers were pinched.
2020 | 03-2020 | Distribution | Employee | Minor injury | Serious harm | Work capacity | Long term shoulder injury has been agravated by manual handling. The employee joined CP with a pre existing condition that then required major surgery to correct.
2020 | 04-2020 | Distribution | Employee | No injury | Fatality | Work capacity | Faultman worked all day, then had a high load at night. He had only just returned to work following the flu. Fell asleep at the wheel while returning home in the morning. Vehicle impacted a Pole but resulted no injury and minor vehicle damage.
2020 | 05-2020 | Distribution | Employee | No injury | Fatality | Falling objects | Quick hitch buckets on an excavator detached. This happened twice. No one was injured.
2020 | 06-2020 | Distribution | Employee | No injury | Serious harm | Personal safety and security breaches | Vegetation crew were felling and chipping. Chipper operator stopped chipping to carry out other work. Second operative climbed into the rear of truck unknown to chipper operator, who returned and started to chip again. The employee in the rear of the truck was not hit by the discharging chip.
2020 | 07-2020 | Distribution | Employee | No injury | Fatality | Fall from height | Ladder fails while employee was using it. Employee managed to jump clear and landed on their feet
2020 | 08-2020 | Distribution | Employee | Minor injury | Serious harm | Personal safety and security breaches | Filling a hot lawn mower not using correct procedure. Mower caught light and the employees gloved hands soaked in petrol caght alight. Hands were badly blistered.
2020 | 09-2020 | Distribution | Employee | No injury | Serious harm | Struck by plant/equipment | Near-Miss Event: Worker installing cable in a trench on the work-site of a third party builder. The weather changed and the wind picked up a sheet of plywood used for a ramp by the builders. The plywood was airborne and passed over the head of the worker who was sitting on the edge of the trench. He heard the noise & felt the wind as it passed over him.
2020 | 10-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Truck trailer within the 4m zone of live conductors.
2020 | 11-2020 | Distribution | Contractor | Minor injury | Serious harm | Struck by plant/equipment | Chainsaw through workers boots.
2020 | 12-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Mobile plant contacting/damaging live conductors
2020 | 13-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | Insecure crossarm on truck which slipped in rough terrain and damaged windscreen
2020 | 14-2020 | Distribution | Employee | Minor injury | Serious harm | Vehicle impacts | mior head injury when Ute went into ditch obsured by long grass.
2020 | 15-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Contractor plant hit underground live cables
2020 | 16-2020 | Distribution | Contractor | No injury | Serious harm | Fall from height | Contractor working at hit, pole step faulty and slipped. Worker secured with harness.
2020 | 17-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Lines deenergised but when tested was eneergy present. Unknown cause.
2020 | 18-2020 | Distribution | Contractor | No injury | Serious harm | Falling objects | Tree fell onto lines, broke line and near public road.
2020 | 19-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Incorrect tree feeling procedure used
2020 | 20-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Incorrect tree feeling procedureused
2020 | 21-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | House removal company -house contactedlines and caused damage.
2020 | 22-2020 | Distribution | Contractor | No injury | Serious harm | Struck by plant/equipment | Truck rolled backwards broke gate in driveway
2020 | 23-2020 | Distribution | Employee | Serious harm | Serious harm | Fall from height | Two employees on pole, one on ladder, one on cross arm, ladder broke, one fell 2m to ground and suffered leg injury, other knocked from work position and received arm injury
2020 | 24-2020 | Distribution | Employee | Serious harm | Serious harm | Struck by plant/equipment | Worker in EWP caught finger between bucket and structure, crushing top of finger
2020 | 25-2020 | Distribution | Employee | No injury | Fatality | Uncontrolled energy release | Worker came into contact with live 400v conductor, received 230V shock. No injury, ECG and check up
2020 | 26-2020 | Distribution | Employee | No injury | Serious harm | Uncontrolled energy release | Stripping conductor for new fuse in pillar, knife contacted live part and flashed. No injury, correct PPE prevented harm
2020 | 27-2020 | Distribution | Employee | No injury | Serious harm | Uncontrolled energy release | A 33kV insulator failed in a sub station during operation of ground equipment, two staff underneath but uninjured by explosion
2020 | 28-2020 | Distribution | Employee | No injury | Fatality | Uncontrolled energy release | Network Controller incorrectly identified the section of line to be earthed and isolated during a fault situation. He directed woth field staff to isolate and then relivened what he thought was the rest of the feeder. This resulted in livening of the section of line down through the worksite.
2020 | 29-2020 | Distribution | Contractor | Minor injury | Serious harm | Fall from height | Worker was approximately 5 rungs up a wooden ladder to access a pole when his ladder failed and he fell.
2020 | 30-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | Protection operated to clear a fault on the feeder to Hurunui Mouth, Cheviot area. SCADA fault current indications suggested the possibility of a line clash with lines down. Patrols revealed a burnt off pole head on a strain pole 2H59. This pole had dropout fuses installed. The asset failure had started a pole fire which burnt the pole right through, causing the pole top to fall onto the ground. This started a grass fire which then set fire to a nearby hedge. FENZ attended to put out the fire. The line was sectionalised and most power was restored.
2020 | 31-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | Three MainPower workers were working to connect a generator truck for a scheduled power outage in Kaiapoi. During the live installation of a temporary SLK disconnector module an electrical arc flash occurred. The electrical arc flash and resultant fire caused significant damage to the LV panel and associated fittings. No injury to workers occurred.
2020 | 32-2020 | Distribution | Employee | No injury | Serious harm | Falling objects | A worker was pulling a PVC encased cable through a transformer platform bracket. The cable flexed, fell out of the worker’s hands and hit a passing cyclist's handlebars (approximately 7 metres away). The cyclist retained control and no injuries were sustained.
2020 | 33-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | A pole failed in a Rangiora residential area, no one was injured or property damaged.
2020 | 34-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | Pole top fire caused 11 kV overhead line to drop down onto the ground. Emergency services were called and attended site. The fire was limited to the pole.
2020 | 35-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | Electrical tracking caused fire to crossarm resulting in 33 kV overhead line to drop onto 11 kV conductors.
2020 | 36-2020 | Distribution | Contractor | Minor injury | Serious harm | Struck by plant/equipment | Whilst accessing a yellow-tagged pole at Antill Farm, a MainPower crane truck became trapped in a creek. A contracted worker was operating a 14 T digger to pull the truck out of the creek, when the recovery strap released, recoiled back, striking the contractor in the face causing serious injury (lacerations to nose, forehead and lip).
2020 | 37-2020 | Distribution | Employee | No injury | Serious harm | Vehicle impacts | While driving a worker has lost conciousness and hit road sign, damaging mirror and left rear tail lights. No injury sustained.
2020 | 38-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | While trimming trees from elevated work platform of V33, gently lowered 2nd boom to access branch, stopped movement ready to trim. After 1 second delay hear loud metal-on-metal snapping sound and simultaneously the platform dropped about 1.5 metres.
2020 | 39-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | Loading the crane unit into cradle to pack up job site. When the crane was rested into the cradle the 2nd large boom ram detached from the fix point and dropped onto the deck.
2020 | 40-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | Pole reported as cable sparking / burning. Investigation revealed two cable cores were bound together with tape and had been chaffing, wearing away the insulation and causing a phase to phase short. The pole which was burnt was confirmed to have self-extinguished.
2020 | 41-2020 | Distribution | Employee | No injury | Serious harm | Falling objects | A tree was found fallen through the Single Wire Earth Return (SWER) line, causing pole 5GT0 to break off at ground-level causing a fire.
2020 | 42-2020 | Distribution | Employee | No injury | Serious harm | Asset failure | A service box caught fire and burnt to the ground.
2020 | 43-2020 | Generation | Employee | No injury | Serious harm | Falling objects | Valve chain wheel and chain fell 5 metres to ground, close to the worker operating this equipment. Kawerau geothermal power station, reference 17026.
2020 | 44-2020 | Generation | Contractor | No injury | Serious harm | Struck by plant/equipment | Fire pump engine started unexpectedly while being serviced by worker. Kawerau geothermal power station, reference 17965.
2020 | 45-2020 | Generation | Contractor | No injury | Fatality | Uncontrolled energy release | Chain block was dragged over a live cable by worker, damaging cable. Mokai geothermal power station, reference 18209.
2020 | 46-2020 | Generation | Contractor | Minor injury | Fatality | Hazardous atmosphere | Suspect that worker was exposed to hydrogen sulphide gas when a tank was being decommissioned. Kawerau geothermal power station, reference 18442.
2020 | 47-2020 | Generation | Contractor | No injury | Serious harm | Hazardous atmosphere | High hydrogen sulphide and carbon monoxide levels from a leaking side valve inner flange. Nga Awa Purua geothermal power station, reference 20558.
2020 | 48-2020 | Generation | Contractor | No injury | Serious harm | Fall from height | Worker slipped and grabbed a handrail. The handrail was not anchored correctly. Maraetai 1 hydro power station, reference 20764.
2020 | 49-2020 | Generation | Contractor | No injury | Serious harm | Work capacity | Worker removed from site following a number of unsafe behaviours. Kawerau geothermal power station, reference 20865.
2020 | 50-2020 | Generation | Contractor | No injury | Fatality | Falling objects | Crane hook raised load, before load was ready to lift. Kawerau geothermal power station, reference 20812.
2020 | 51-2020 | Generation | Contractor | Serious harm | Serious harm | Struck by plant/equipment | Worker suffered broken leg when it was trapped between moving screen cleaner and a fixed railing . Aratiatia hydro power station, reference 21336.
2020 | 52-2020 | Generation | Contractor | Serious harm | Fatality | Fall from height | A Contractor fell from the turbine pit access area on to the draft tube platform, after a temporary barrier, which he was reaching over it, gave way. This was a fall of approximately 5m, in two stage
2020 | 53-2020 | Generation | Employee | No injury | Serious harm | Struck by plant/equipment | The team were attempting to identify a noise that the lift was making. To do this one member of the team was on the ladder observing whilst two more inside drove it down. Feet were caught between the ladder and the lift.
2020 | 54-2020 | Generation | Employee | Minor injury | Serious harm | Struck by plant/equipment | Crushed finger during pitch ram exchange while working on the platform off the front of the hub
2020 | 55-2020 | Distribution | Employee | Minor injury | Serious harm | Hazardous substances/materials | A staff member ignited a gas torch after cleaning it with a solvent, which accidently set some nearby cloth alight. Another worker grabbed the bottle of open solvent which spilled onto the burning cloth and over his hands and instantly ignited the spilled solvent causing burns to the staff members hands.The quick response of others and the close proximity of emergency response gear minimised injury impact.
2020 | 56-2020 | Distribution | Employee | No injury | Serious harm | Falling objects | Felled Tree swung and hit PI
2020 | 57-2020 | Distribution | Employee | No injury | Fatality | Uncontrolled energy release | flash over occurred tripping the 11KV CB
2020 | 58-2020 | Distribution | Employee | No injury | Fatality | Uncontrolled energy release | LV livened at 400 Volts
2020 | 59-2020 | Distribution | Employee | No injury | Serious harm | Uncontrolled energy release | Arc flash while operating 11kV temp disconnectors
2020 | 60-2020 | Distribution | Employee | No injury | Serious harm | Uncontrolled energy release | Switching permit incorrect
2020 | 61-2020 | Distribution | Employee | No injury | Serious harm | Vehicle impacts | Polaris turned onto side
2020 | 62-2020 | Distribution | Employee | No injury | Serious harm | Uncontrolled energy release | Incorrect switching on Access permit
2020 | 63-2020 | Distribution | Contractor | No injury | Fatality | Uncontrolled energy release | A contracted worker received an electric shock while testing a high voltage transformer. The worker was medically assessed and was unhurt.
2020 | 64-2020 | Distribution | Contractor | Serious harm | Serious harm | Personal safety and security breaches | Trip and fall on same level. Worker was walking on scaffolding and fell onto a hip that had previously been fitted with a prosthetic joint. Due to the impact, his femur was fractured resulting in surgery and lost time.
2020 | 65-2020 | Distribution | Contractor | No injury | Serious harm | Hazardous substances/materials | Gas leak encountered after hot work near gas pipe.
2020 | 66-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Contractor Electric Shock from 11kV Pole
2020 | 67-2020 | Distribution | Contractor | Minor injury | Fatality | Fall from height | LTI - Fall from ladder
2020 | 68-2020 | Distribution | Contractor | Minor injury | Fatality | Falling objects | LTI - TX Fell from height knocking IP from ladder
2020 | 69-2020 | Distribution | Contractor | Minor injury | Fatality | Fall from height | RWI - Fall from ladder while descending
2020 | 70-2020 | Distribution | Contractor | Serious harm | Fatality | Vehicle impacts | LTI - Subcontractor vehicle rear ended
2020 | 71-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Cable strike UG Live 11kv Feeder
2020 | 72-2020 | Distribution | Contractor | Minor injury | Fatality | Fall from height | LTI - Fall from 5m cliff
2020 | 73-2020 | Distribution | Contractor | Minor injury | Serious harm | Falling objects | RWI - Bouncing wood struck worker in head
2020 | 74-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Switching for re-conductoring shut down - Arc Flash
2020 | 75-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | Vehicle tangled in 11kV lines
2020 | 76-2020 | Distribution | Employee | Serious harm | Fatality | Vehicle impacts | Crew were patrolling 33kV line looking for a transient fault - descending farm track in 4x4 vehicle. Wet conditions caused the vehicle to veer towards edge of track and vehicle slid sideways down steep slope before rolling over and coming to rest on the drivers side.
2020 | 77-2020 | Distribution | Employee | No injury | Serious harm | Falling objects | 11m Busck Pole Slid Off Truck Onto Road
2020 | 78-2020 | Distribution | Employee | No injury | Fatality | Uncontrolled energy release | Transformer installation missing the neutral causing property damage
2020 | 79-2020 | Distribution | Employee | No injury | Serious harm | Vehicle impacts | Rolled truck reversing into ditch
2020 | 80-2020 | Distribution | Contractor | No injury | Fatality | Uncontrolled energy release | Electric Shock Clearing Asphalt around front of Linkbox and Cables
2020 | 81-2020 | Distribution | Employee | Minor injury | Fatality | Fall from height | Climbing ladder on pole when just about at top ladder cracked and twisted and I fell from pole to the ground
2020 | 82-2020 | Distribution | Contractor | No injury | Fatality | Uncontrolled energy release | Contractor cut 11kV cable instead of 400v cable
2020 | 83-2020 | Distribution | Contractor | No injury | Fatality | Vehicle impacts | Arborist Contractor Contacted Powerlines
2020 | 84-2020 | Distribution | Employee | Serious harm | Serious harm | Uncontrolled energy release | Injury to Eye (LTI) - Attempting to move an existing earth rod
2020 | 85-2020 | Distribution | Employee | Minor injury | Fatality | Falling objects | A branch cut by an arbourist fell from 6 meters and then bounced and travelled 8meters and hit a ground crew member in the head
2020 | 86-2020 | Distribution | Employee | Minor injury | Serious harm | Vehicle impacts | LUV rolled onto its side muddy farm track whilst following a excavator, driver was not wearing seat belt was ejected out of LUV and his foot was injured
2020 | 87-2020 | Distribution | Employee | Minor injury | Serious harm | Work capacity | Damaged rotator Cuff while tensioning a HV line
2020 | 88-2020 | Distribution | Contractor | No injury | Fatality | Falling objects | Crane toppled - overloaded - lack of proper lift planning
2020 | 89-2020 | Distribution | Contractor | No injury | Fatality | Personal safety and security breaches | Shots fired at Metering tech
2020 | 90-2020 | Distribution | Contractor | No injury | Serious harm | Asset failure | Wheel came off ute while driving
2020 | 91-2020 | Distribution | Staff | No injury | Serious harm | Vehicle impacts | Vehicle slid off road towing trailer
2020 | 92-2020 | Transmission | Contractor | No injury | Serious harm | Uncontrolled energy release | A spare transformer being moved down a traverser track breached the MAD from an adjacent live 110 kV circuit breaker.
2020 | 93-2020 | Transmission | Contractor | No injury | Serious harm | Asset failure | This incident involved a fibreglass cable snake coming close to contacting a live HV conductor after it unexpectedly flipped up over a protective barrier.
2020 | 94-2020 | Transmission | Contractor | No injury | Fatality | Uncontrolled energy release | Sub contractor using digger to pull out redundant power cables, incorrectly pulled on live 22kV cable causing the cable to blow up
2020 | 95-2020 | Transmission | Contractor | No injury | Serious harm | Personal safety and security breaches | Whilst excavating for a new 110kV cable trench along side the existing 33kV cable route, the 8T excavator bucket has damaged the outer sheath of the existing 33kV cable. Work ceased immediately.
2020 | 96-2020 | Transmission | Contractor | No injury | Serious harm | Personal safety and security breaches | A tower painter returned a permit to the permit issuer, but then continuing to work on the towers without a modified or new permit being issued. On discovery, all outage work was stopped, staff were cleared from the lines, and all temporary earths were removed.
2020 | 97-2020 | Transmission | Contractor | No injury | Serious harm | Personal safety and security breaches | An apparent miscommunication occurred between NGOC and Powerco during switching operations. Northpower were informed that the feeder they were going to be working on was isolated when in fact it had just been offloaded. This was identified when a voltage detection device was used to prove safe access to the equipment.
2020 | 98-2020 | Transmission | Contractor | No injury | Serious harm | Personal safety and security breaches | The second incident involved a line crew completing maintenance work. An internal audit showed the team had completed work on one structure, after testing and applying earths, however on arrival at the second structure the team failed to retest before installing earths.
2020 | 99-2020 | Transmission | Contractor | No injury | Fatality | Uncontrolled energy release | A maintenance switcher tested the top earthing connection on a circuit breaker (CB) to prove it was deenergised. When he attempted to attach the portable earth to the earthing horn he didn't realise that part of the CB below was still energised. The sheath of the portable earth came into close contact with the live equipment resulting a flashover. The switcher was unhurt, but was taken for a precautionary medical assessment.
2020 | 100-2020 | Generation | Employee | No injury | Serious harm | Personal safety and security breaches | Small water leak was discovered from the generator priming pipe. A Work Authority was issued, and the plant isolated to carry out the repair. In reviewing the task and competence requirements it was identified that this type of work should only be done by a qualified welder.
2020 | 101-2020 | Generation | Employee | No injury | Serious harm | Personal safety and security breaches | Failure to isolate water supply before starting work.
2020 | 102-2020 | Generation | Contractor | No injury | Fatality | Fall from height | Contractors working at height without harnesses.
2020 | 103-2020 | Generation | Employee | No injury | Fatality | Hazardous atmosphere | Welding without hot work permit
2020 | 104-2020 | Generation | Employee | No injury | Fatality | Personal safety and security breaches | Removing the Thrust Retaining Collar of the G1 Thrust bearing by heating with Oxy / LPG to rapidly heat the collar. (with OXY / LPG set belonged to contractor). Work was complete and the nozzle set in the holder. Gas set moved to a nearby location ‘out of the way’. Returning to the station the following day the fallen nozzle was seen on nearby ground level open cable tray and damage to cables noted. Potential fire
2020 | 105-2020 | Distribution | Contractor | Serious harm | Fatality | Uncontrolled energy release | Contractors were preparing to remove overhead temporary in-line disconnectors. When applying cover-up mats to the in-line disconnectors and overhead lines, the link unexpectedly opened and drew an arc, which lead to a flashover. Both employees were wearing their PPE and following the correct
2020 | 106-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | The crew was unloading a transformer and working in a live lane with no traffic management set up when they were issued a stop work order and found the site to be non-compliant.
2020 | 107-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | Carrying out pole work on a sloping road. An Elevated Work Platform (EWP) vehicle was parked on a sloped road with the rear of the vehicle facing downward. When stabilising the vehicle, the rear portion of the vehicle was lifted first, causing the vehicle to become mobile and slide approximately 20 metres downhill. The outrigger caught the kerb, causing it to bend and enabled the vehicle to come to a slow stop.
2020 | 108-2020 | Distribution | Contractor | Minor injury | Fatality | Uncontrolled energy release | Whilst identifying 400v DC abandoned cables person involved struck 11kV feeder resulting in arc flasher and burns. Incident is a 3rd party damage incident
2020 | 109-2020 | Distribution | Contractor | Minor injury | Fatality | Uncontrolled energy release | During phase rotation testing, when contact was made on the transformer bushings a minor arc flash occurred.
2020 | 110-2020 | Distribution | Contractor | Serious harm | Fatality | Fall from height | Person standing on inspection step on concrete truck, slipped and unable to steady or grasp the handrail fell to the ground. Person struck his head before landing on his shoulder.
2020 | 111-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | An unattended traffic management truck rolled down hill and crossing left to right came into contact with a small tree on the opposite berm.
2020 | 112-2020 | Distribution | Contractor | Minor injury | Fatality | Uncontrolled energy release | A cable Jointer while cutting through a LV cable riser, which had been lowered to the ground, suffered a burn to his hand and minor burns to his lower face and lips when a flashover occurred.
2020 | 113-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | Driving MEWP to site, the driver looked away briefly while driving over a hill and when he looked back again the traffic in front had stopped. Driver applied brakes but wheels locked up and truck hit rear of stationary car causing significant damage to car but only minor damage to truck.
2020 | 114-2020 | Distribution | Contractor | No injury | Serious harm | Personal safety and security breaches | Removing Gums adjacent to 11kV power lines while attempting to push the tree over the operator has lost control of the tree which fell in the opposite direction across the road and into the power lines causing an outage.
2020 | 115-2020 | Distribution | Contractor | No injury | Serious harm | Uncontrolled energy release | Clearing trees from adjacent to LV/HV Powerlines using MEWP. To re-position the MEWP the driver drove forward set the outriggers then while the bucket operator manoeuvred the boom over the top of the 11kV lines to reach the trees it started to rain and the wind increased. The lower section of the boom contacted the outside phase of 11kV lines causing electricity to travel through the truck and the earthpin which the groundsperson was re-deploying.
2020 | 116-2020 | Distribution | Public | Minor injury | Serious harm | Uncontrolled energy release | Member of the public advised that someone had touched the overhead line whilst working at their home and felt a shock from it.
2020 | 117-2020 | Distribution | Contractor | No injury | Serious harm | Fall from height | Construction worker went to gain access to a scaffolding ladder to a basement. As the PI stepped down onto the step to access the ladder his foot slipped, and he fell approx. 1m to the ground floor.
2020 | 118-2020 | Distribution | Contractor | No injury | Serious harm | Vehicle impacts | The site was shut down and a stop work order issued due to being unsafe for public and unsuitable TTM.
2020 | 119-2020 | Distribution | Contractor | No injury | Serious harm | Falling objects | Moving cabinet (100-150kg) to ground, cabinet fell over and hit workers knee/leg
2020 | 120-2020 | Distribution | Employee | Serious harm | Serious harm | Uncontrolled energy release | Employee received flash burns to his hands following a flash over event in a LV panel of transformer
2020 | 121-2020 | Distribution | Contractor | Minor injury | Serious harm | Uncontrolled energy release | A 400V crutch joint service main was identified as requiring repair however the repair could not be carried on the night of the fault and was rescheduled. The installation fed from the failed crutch joint was a fire station so had generator supply. A fault repair job pack was created showing the points of isolation and was criculated within the faults team based within the region where the fault was. The repair again could not occur on the scheduled evening at the request of the fire service so was further re-scheduled for the next evening. Due to workload the faultmen based in the region were tasked on other work and the assigned cable jointer had changed shifts the evening of the work. A faultman from another region was tasked to isolate the cable however had no visibility of the fault repair job pack. Information was supplied by GIS staff on where the isolation points were however the fault man failed to correctly isolate the links supplying the cable. The faultman did not test the fire station or at the next link box to confirm the cable was isolated. The faultman verbally confirmed the cable was isolated. The cable jointer having been told the cable was isolated observed the configuration in the joint hole was as expected from the configuration showing in GIS. The cable jointer did not request a technician to positively Identify the cable and also did not spike the cable. Believing the cable was de-energised he cut into the cable with a reciprocating saw causing a flashover resulting in minor burns to the forearm and hand.
2020 | 122-2020 | Generation | Contractor | No injury | Serious harm | Uncontrolled energy release | During shotcreting operation the team experienced a blockage in the line. During a move and securing operation the air was called to be turned on by the nozzleman without realising the valves further along were still open. Cleaner ball and shotcrete shot out and hit the contractors face, blowing his safety glasses and hard hat off.
2020 | 123-2020 | Generation | Contractor | Serious harm | Serious harm | Fall from height | Contrator tripped and fell resulting in fractured elbow
Note on F123: Bridget Bourke: Fatality?
Note on F128: Bridget Bourke: Fatality
Note on E133: Bridget Bourke: Serious harm
Note on F133: Bridget Bourke: Serious harm
Note on G133: Bridget Bourke: Or Work related ill health?
Note on G144: Bridget Bourke: Work related ill-health?
Note on G145: Bridget Bourke: Work related ill health
Note on F160: Bridget Bourke: Fatality
Note on G160: Bridget Bourke: Electricity?
Note on G168: Bridget Bourke: Working at heights?
Note on G193: Bridget Bourke: Driving
Note on F194: Bridget Bourke: Fatality?
Note on F195: Bridget Bourke: Fatality
Note on G196: Bridget Bourke: Electricity
Note on G208: Bridget Bourke: Hazardous materials
Note on G209: Bridget Bourke: Asset Failure
Note on G236: Bridget Bourke: Driving
Note on G248: Bridget Bourke: Driving?
Note on F251: Bridget Bourke: Fatality?
Note on F261: Bridget Bourke: Serious harm? Torn achilles?
Note on G261: Bridget Bourke: Could be working at heights?
Note on G262: Bridget Bourke: Work related ill-health?
Note on G354: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G355: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G356: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G357: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G358: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G359: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G360: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G361: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G362: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G363: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G367: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Electricity"
Note on G370: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Electricity"
Note on G371: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Electricity"
Note on G374: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Electricity"
Note on G376: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Contact with Electricity"
Note on G377: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Electricity"
Note on G378: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from "Electricity"

## List of Critical Risks
2018-2019 Critical risk | 2020 Critical Risks
Asset failure | Uncontrolled energy release
Confined spaces | Fall from height
Driving | Falling objects
Electricity | Asset failure
Hazardous materials | Hazardous substances / materials
Lone working | Hazardous atmosphere
Mobile powered plant | Work capacity
Traffic management | Personal safety and security breaches
Work at heights | Struck by plant, equipment
Work-related ill-health | Vehicle impacts
Not listed (specify in narrative) | Waterways