## For publication in report
Event No. | Industry sector | Personnel involved | Critical risk | Potential consequence | Actual consequence | Description of event
2018-1 | Distribution | Employee | Asset failure | Fatality | No injury | Employees were removing an old pole during removal the pole broke at ground level causing the pole to fall to the side, the employees has set up an exclusion zone for this and no employees were in the zone.
2018-2 | Distribution | Employee | Asset failure | Serious harm | Minor injury | Cracked Insulator broke and a piece fell on employees head while wearing his hard hat
2018-3 | Distribution | Employee | Asset failure | Serious harm | No injury | Conductor broke and fell to the ground
2018-4 | Distribution | Employee | Asset failure | Serious harm | No injury | Opened HV vertical switch Porcelain Insulator fell from ABS onto left foot just missing shoulder on its decent
2018-5 | Distribution | Employee | Asset failure | Serious harm | No injury | Insulator broke during operation of ABS hitting employee no injury
2018-6 | Distribution | Employee | Driving | Fatality | No injury | Trailer pin came free whilst driving on gravel road
2018-7 | Distribution | Employee | Driving | Fatality | No injury | Loss of control of vehicle
2018-8 | Distribution | Employee | Driving | Fatality | Serious harm | Reversing down a farm track and truck rolled down a bank. Whilst rolling an employee's tip of his finger was severed. Truck was submerged in river.
2018-9 | Distribution | Employee | Driving | Serious harm | No injury | Uncontrolled movement of truck.
2018-10 | Distribution | Employee | Driving | Serious harm | No injury | Boom of crane got stuck under low bridge
2018-11 | Distribution | Employee | Driving | Fatality | No injury | Employee identified damage to ladder rack prior to driving, ladder could have had the potential to come free from moving vehicle had this not been identified
2018-12 | Distribution | Employee | Electricity | Fatality | No injury | Tree "barbers chair" split whilst being felled causing it to fall in an unintended direction, hitting and breaking live 11kV powerline causing loss of power to customers
2018-13 | Distribution | Employee | Electricity | Fatality | No injury | Pillar box found smoking and fizzing when worker when to replace it after being hit by car. On closer inspection wires inside found to be wrapped in tape that may contain metal.
2018-14 | Distribution | Employee | Electricity | Fatality | No injury | Arc cutting jumper
2018-15 | Distribution | Employee | Electricity | Fatality | No injury | Utility worker attempted to cut through a live low voltage (240 volt) single core 16mm² copper neutral screened house service cable.
2018-16 | Distribution | Employee | Electricity | Fatality | No injury | Trainee cable jointer received minor electric shock between bare right hand and exposed right elbow, while stripping outer sheath on disconnected LV mains cable for testing purposes.
2018-17 | Distribution | Employee | Electricity | Fatality | No injury | Two crews straightening a pole transformer, TMP in place and monitored by Traffic Management Services. Stock Truck came through and clipped wire. Both truck driver and crews checked to establish no injuries.
2018-18 | Distribution | Employee | Electricity | Fatality | No injury | Employee cut through an underground cable, without positively identification, assumption was it was redundant, turned out to be an in-service communication cable however it could have been a single leg paper lead cable.
2018-19 | Distribution | Employee | Electricity | Fatality | No injury | Arc-flash caused due to incorrect operation HV equipment
2018-20 | Distribution | Employee | Electricity | Serious harm | No injury | Near miss involving the foreman attempting to hand back an access permit to control room that all men were clear of the line and it was clear to liven. Other crew was still working on spur line and overheard conversation on RT. Contacted control room and foreman to notify that they were still working on the line
2018-21 | Distribution | Employee | Electricity | Serious harm | No injury | RMU operated remotely while a field operative was accessing it
2018-22 | Distribution | Employee | Electricity | Serious harm | No injury | During pre-livening checks of a new metering unit, someone had changed the CB relay settings to a different setting from those specified by the engineer
2018-23 | Distribution | Employee | Electricity | Serious harm | No injury | Gas switch closed in error
2018-24 | Distribution | Employee | Electricity | Serious harm | No injury | Hit an unidentified service whilst driving an earth pin into the ground
2018-25 | Distribution | Employee | Electricity | Serious harm | No injury | Attending fault. Opened pillar to assess fault and lost control of pliers that dropped onto live connections causing a phase to phase flash over. Worker was distracted by co-worker who was talking and lost concentration momentarily at a critical stage of the process. Worker returned to work the following day on light duties. As a result of this incident all live work was suspended, which eliminates the risk of re-occurrence of this incident. A separate work stream has been established to consider the subject of future live work including procedures etc. This is incident was reportable to WorkSafe NZ as they consider a "flash over" to be the same as electrocution. They have advised that they will take no further action on this incident.
2018-26 | Distribution | Employee | Hazardous materials | Serious harm | Serious harm | Slipped on substance on floor whilst carrying cable drum on arm, fracturing arm
2018-27 | Distribution | Employee | Lone working | Operational (Major) | No injury | Redundancy issue for on call staff who are unwell
2018-28 | Distribution | Employee | Lone working | Serious harm | No injury | Call centre received threatening phone calls from customer on fault line who had no power. Faultman could have been at risk if threats had been real had they attended property to investigate unaccompanied. Went escorted by police
2018-29 | Distribution | Employee | Lone working | Serious harm | No injury | Verbal treat to staff member treat of shooting
2018-30 | Distribution | Employee | Work at heights | Serious harm | Minor injury | Side rail of ladder fractured while employee was descending. Employee fell to ground
2018-31 | Distribution | Employee | Work at heights | Serious harm | Minor injury | Employee fell from ladder sustaining fractures and other injuries. Worksafe was notified, and did not investigate further.
2018-32 | Distribution | Employee | Work at heights | Serious harm | No injury | Fall from EWP
2018-33 | Distribution | Employee | Work at heights | Serious harm | No injury | Ladder failed
2018-34 | Distribution | Employee | Work at heights | Serious harm | No injury | Falling object from pole stuck employee on leg (spanner)
2018-35 | Distribution | Employee | Work-related ill-health | Serious harm | Minor injury | An employee sprained his back while carrying a drum of cable in the yard. The employee had to undergo short series of osteo treatment.
2018-36 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | Whilst working under a building stretched to complete a task and hurt shoulder.
2018-37 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | While working up pole reached out to use come along and strained back.
2018-38 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | Line mechanic unbounding conductor from fallen pole dislocated right shoulder and strained left shoulder when trying to raise the wire in the air.
2018-39 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | Line mechanic injured shoulder while manually pulling overhead conductor.
2018-40 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | Utility arborist injured shoulder while cutting and holding branches.
2018-41 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | Storeman rearranging fish bins of square washers on pallet. Felt lower abdominal strain and tightness.
2018-42 | Distribution | Employee | Not listed (specify in narrative) | Fatality | No injury | While attending a fault and proceeding to cross the bridge to gain access to the network, the bridge gave way under the EWP, stranding the vehicle on the bridge. (no signs were at bridge or along road to indicate the bridge could not be driven on)
2018-43 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Whilst tensioning conductor the line broke hitting the employee on both hand and face
2018-44 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Cable drum crashed from Jinker whilst being winched on
2018-45 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Ladder was blown off the pole by the wind before it had been tied down
2018-46 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Certain Reyrolle switch gear have an Operating Restriction placed on them that say they can only be operated with the complete RMU de-energised. Earth Switch was closed with the RMU alive. Isolation was being provided for a cable fault.
2018-47 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Identified guarding bypassed on bench mounted grinder
2018-48 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Serious harm | Straining up conductor and started pulling when a join in the conductor failed causing conductor to snap and come along thrown back towards worker
2018-49 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Serious harm | Hit on head by tree limb resulting in concussion - reported to Worksafe (vegetation worker - not listed in critical risk)
2018-50 | Distribution | Contractor | Asset failure | Fatality | Production Loss (minor) | Pole incorrectly installed (Worksite shut down)
2018-51 | Distribution | Contractor | Asset failure | Serious harm | No injury | Low HV Line across road, low enough for truck to pull down. Post recent works.
2018-52 | Distribution | Contractor | Driving | Fatality | No injury | 2 crew stranded in vehicle driven into flooded river at night during storm event. Swam to safety.
2018-53 | Distribution | Contractor | Electricity | Fatality | No injury | 11kV line under works contacted live 33kV Line. Potential for Multiple fatalities.
2018-54 | Distribution | Contractor | Electricity | Fatality | No injury | AP Issued with HV isolations and no earths
2018-55 | Distribution | Contractor | Electricity | Fatality | No injury | Contractor working on network without a permit
2018-56 | Distribution | Contractor | Electricity | Fatality | No injury | As part of a job to supply power to a new Car Charger, a pillar box was to be installed and connected into a spare de-energised 400V link cable. Three of the cables feed out of the transformer were exposed and one of them was identified as the de-energised cable. It was spiked and cut through on one side (At this stage there was no indication the cable was live) they started to cut the other side of the cable when there was a flash.
2018-57 | Distribution | Contractor | Electricity | Fatality | No injury | Contractor putting in Telco pole, with in 4m Mads, Plant also not bounded, no safety observer or work authority. Discussed with Contractor, the correct procedure and requirements for working within the Mads, site was shut down further action to be sorted out with PNL staff.
2018-58 | Distribution | Contractor | Electricity | Fatality | No injury | Tree workers made inadvertent contact with LV overhead conductors causing tripping
2018-59 | Distribution | Contractor | Electricity | Production Loss (major) | Production Loss (minor) | A parallel was made between 33kV Feeders and the ARs in line with these feeders did not have the Earth Fault Pickup disabled by the controller
2018-60 | Distribution | Contractor | Electricity | Serious harm | Minor injury | When undertaking circuit breaker pressure testing on the equipment, a contractor employee came into contact with the live test lead from which he received an electric shock. The subsequent injury developed overtime into a lost time injury.
2018-61 | Distribution | Contractor | Electricity | Serious harm | No injury | Were following LV Cable and uncovering with shovel, checking no danger - services, cables, gas etc. Uncovered and exposed LV joint. One final scoop to clear fill and digger hit 11kV cable.
2018-62 | Distribution | Contractor | Electricity | Serious harm | No injury | Contractor carrying out work outside transformer around hit the feeder. They were digging a hole to install a LV link box outside the transformer substation site, however they stuck the C02 feeder cable and caused it to fail.
2018-63 | Distribution | Contractor | Electricity | Serious harm | No injury | Employee called to construction site where security guard and another third party received an electric shock from a fence at Victoria Square. They were not injured. The fault was found to be due to a neutral not connected to the bus bar in a distribution box. We notified Worksafe of the event and they elected not to investigate further.
2018-64 | Distribution | Contractor | Mobile powered plant | Fatality | No injury | Contractor was undertaking pole replacement in conjunction with utilizing an excavator during this process the operator swung the excavator around making contact with an old pole causing the pole to fail
2018-65 | Distribution | Contractor | Mobile powered plant | Serious harm | No injury | Contractor observed at risk working under a suspended load
2018-66 | Distribution | Contractor | Mobile powered plant | Serious harm | No injury | Contractors placing themselves in the line of fire when standing in the swing arc of an excavator.
2018-67 | Distribution | Contractor | Mobile powered plant | Serious harm | Serious harm | Tree Work Clearing Private pine plantation away from line. Digger pushed over a hanging tree which fell between a number of stumps. When the digger moved the tree it created tension breaking the tree and sending a large splinter flying which struck one of our arborists in the left side of his head. He was taken to hospital as a precaution.
2018-68 | Distribution | Contractor | Work at heights | Serious harm | No injury | Workers were conducting pole change out process and were observed by not employing a 100% restraint while working at heights.
2018-69 | Distribution | Contractor | Work at heights | Serious harm | No injury | Contractor observed displaying at risk behaviour while working at heights
2018-70 | Distribution | Contractor | Work at heights | Serious harm | No injury | Contractor observed displaying at risk behaviour working at heights
2018-71 | Distribution | Contractor | Work-related ill-health | Serious harm | Minor injury | Contractor suffered a neck strain which required frequent doctor visits. A reminder to all contractors of their contractual requirements was sent out.
2018-72 | Distribution | Contractor | Work-related ill-health | Serious harm | Minor injury | A subcontractor reported that he had strained his lower back while moving fence barriers on a residential external connection.
2018-73 | Distribution | Contractor | Work-related ill-health | Serious harm | Minor injury | A contractor twisted his lower back while dragging branches to the chipper.
2018-74 | Distribution | Contractor | Work-related ill-health | Serious harm | Minor injury | A contractor was carrying his ladder when a gust of wind caught the ladder and caused his to twist his shoulder.
2018-75 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | Minor injury | A contractor employee cut the underside soft tissue of his thumb while stripping a cable. Worksafe has closed the file and is not investigating further.
2018-76 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | Minor injury | This medical treatment injury involved a contusion / haematoma that was initially reported as pain/discomfort but pain continued and a MRI was required.
2018-77 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | Minor injury | A contractor was alighting from the back of a crane truck. He tripped and fell forward hitting his knee on a concrete pole.
2018-78 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | No injury | Result of a splinter that had become infected, the injury required two doctor visits for cleaning and removing the splinter.
2018-79 | Generation | Employee | Asset failure | Fatality | No injury | The CHF on the wellhead had two threaded side outlets that were filled with cast threaded bull plugs. These plugs were exposed to wellbore pressure. The well in question had been off pressure for a number of years and was recently abandoned (a few months back). During the post-abandonment wellhead removal, during hammering to the top face of the CHF, one of the plugs just fell off. It is reported that it had not been hit or knocked. The failure was a fracture of the steel surface part-way down the engaged threaded section. If the well had been under pressure, the bull plug could have turned into a high speed projectile.
2018-80 | Generation | Employee | Asset failure | Fatality | No injury | Was informed that the top sheave and part of the support bracket from the mast of the installation had fallen from the masthead into the cellar. The components that have come loose have fallen approximately 8 meters and landed in the well cellar, no one was injured in this incident but given that the assembly that fall has an approximate weight of 10kg there was the potential under a different set of circumstances (had someone been present at the time of a failure) for major injury.
2018-81 | Generation | Employee | Asset failure | Fatality | No injury | On Wednesday morning following the gale force winds the during the evening / night of Tuesday, a fixed vertical ladder cage on the western side of the cooling tower, was found to have broken off and was laying on the gravel beside the ladder. This ladder is primarily used as a secondary escape exit from the upper levels of the cooling tower. The ladder and cage are of composite fibreglass construction.
2018-82 | Generation | Employee | Driving | Fatality | Minor injury | Employee suffered minor injuries, when the vehicle they were driving was struck by an oncoming vehicle (driven by member of public) that crossed the centre line
2018-83 | Generation | Employee | Driving | Fatality | No injury | Employee had to take evasive action, when an oncoming vehicle (driven by member of public) crossed the centre line
2018-84 | Generation | Employee | Driving | Fatality | No injury | Employee had to take evasive action, when an oncoming vehicle (driven by member of public) crossed the centre line
2018-85 | Generation | Employee | Electricity | Fatality | No injury | Refilling of 110/11 kv transformer whilst energised without correct work control procedures in place.
2018-86 | Generation | Employee | Lone working | Serious harm | No injury | Door to Door employee entered a property and was assaulted by the resident of the property when he pushed and kissed her. The employee was not hurt but very shaken by the event.
2018-87 | Generation | Employee | Work at heights | Fatality | No injury | A hub hatch was found on the ground. The hatch was not engaged fully into the hole and was not double checked after it was closed.
2018-88 | Generation | Employee | Work at heights | Serious harm | No injury | An employee descended and ascended a turbine without a harness and no means of communication.
2018-89 | Generation | Employee | Not listed (specify in narrative) | Fatality | No injury | Sored energy/Work Control Procedures - Worker went to work on wrong side of isolation, stopped by another member of the work party
2018-90 | Generation | Contractor | Asset failure | Fatality | No injury | Generator overspeed event while commissioning. The overspeed device tripped the unit at 140% speed, but the overshoot caused the unit to reach 160% of rated speed
2018-91 | Generation | Contractor | Confined spaces | Fatality | No injury | Occupational diver failed breathe alcohol test
2018-92 | Generation | Contractor | Electricity | Serious harm | No injury | A contractor Balance of Plant Operator accessed a low voltage kiosk while energised to carry out an inspection. The signage on the kiosk clearly stated that the Transformer should be de-energised and earthed before opening due to risk of arc flash.
2019-01 | Distribution | Contractor | Hazardous materials | Serious harm | Serious harm | Non Electrical - A large rock was to be placed in the garden outside Alpine House, so that a plaque could be fixed to it to mark the formal opening of the building. The rock has to be lifted into the approximare location. While manoeuvring the rock into the best orintation, the lifting strops caught the involved persons hand. The involved person requested the rock be lowered right away. Once the strops had been realeased the nature of the injury was clear partical de gloving and a crush injury to the persons finger.
2019-02 | Distribution | Employee | Electricity | Serious harm | No injury | Near miss involving a member of staff attending a fault, he noticed a spark on the cross-arm and as he climbed the ladder with his LV gloves on he tested the the cross-arm and as he climbed the ladder with his LV gloves on he tested the cross-arm and found it was live
2019-03 | Distribution | Employee | Electricity | Serious harm | No injury | Near miss involving a worker at a fault situation and had one blown HV fuse. He noticed earth lead had come off earth pin and assumed this was the issue. He noticed earth lead had come off earth pin and assumed this was the issue. He opened the other HV fuses at the Tx, fixed the earth lead and closed in the HV fuses. As he did he noticed sparking at the mains entry point at the house. So he pulled the HV fuses straight away and tagged to get mains entry fixed ASAP.
2019-09 | Distribution | Employee | Traffic management | Fatality | Minor injury | OHL worker within defined traffic management area was struck by member of the public who was on his phone while driving through a restricted speed area.
2019-10 | Distribution | Employee | Mobile powered plant | Serious harm | Minor injury | Civil worker was struck a glancing blow by a mini excavator while it was trafficking through the work site
2019-11 | Distribution | Employee | Mobile powered plant | Serious harm | Minor injury | Installation of cable hauling rope into cable ducts. A superceded installation practice was being utilised by an inexperienced worker. The workers hand was injured and a minor fracture to the wrist was sustained. The worker was wearing gloves.
2019-12 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | While restringing an overhead line repair one of the clamps holding the line slipped and narrowly missed the linesmans face
2019-13 | Distribution | Employee | Not listed (specify in narrative) | Fatality | No injury | Two faultman working at night were threatened by the tenant with a knife.
2019-14 | Distribution | Contractor | Driving | Fatality | Minor injury | Contractor fell asleep at the wheel while driving to work and left the road and crashed.
2019-15 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Cable jointing tooling slipped while carryining out jointing operations.Cut to hand. Stiches required
2019-16 | Distribution | Contractor | Electricity | Fatality | No injury | Contractor carrying out directional drilling hits HV underground cable
2019-17 | Distribution | Employee | Electricity | Fatality | No injury | Incorrect switching procedures
2019-18 | Distribution | Employee | Electricity | Fatality | No injury | Earthing transformer closed on earthing pin that was innadvertantly left in place following commissioning tests
2019-19 | Distribution | Employee | Electricity | Fatality | No injury | LV lines found to be still energised during works
2019-20 | Distribution | Employee | Electricity | Serious harm | No injury | Auger to install new pole hits LV service cable.
2019-21 | Distribution | Contractor | Electricity | Serious harm | No injury | Contractor carrying out directional drilling hits LV underground cable
2019-22 | Distribution | Employee | Driving | Fatality | No injury | There have been a number of trailer related incidents. Usually the trailer detaches from the towing ball and is caught by the breakaway chains.
2019-23 | Distribution | Employee | Work-related ill-health | Serious harm | Serious harm | This event is unusual, in that it was not a serious event but led to a serious infection (cellulitis). Essentially our worker bumped his leg against a door sill while getting in, and that bump turned into cellulitis. There was no critical risk involved, no activity that was preventable as such, and the opportunities for learning were only around early diagnosis through monitoring of an injury.
2019-24 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Serious harm | worker sufferred a crush injury to their finger tip, resulting in the loss of finger tip, whill working on a pneumatic tool. The worker attempted to change the tool head while the tool was connected to air line. The tool has activiated as they leant over it crushing their finger tip.
2019-25 | Distribution | Employee | Falls | Serious harm | Serious harm | Slilpped on uneven ground in riverbed, outstretched hand to break fall which resulted in a fractured schapoid bone in the wrist. This was a university student on an internship.
2019-26 | Distribution | Employee | Driving | Fatality | No injury | Sunstrike whilst driving nearly caused a collision.
2019-27 | Distribution | Employee | Driving | Fatality | No injury | Other speeding vehicle nearly caused a motor vehicle accident.
2019-28 | Distribution | Employee | Driving | Serious harm | No injury | Almost hit from behind by a vehicle in an 80 kph zone whilst waiting to turn right into work
2019-29 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Foot slipped when getting out of vehicle
2019-30 | Distribution | Employee | Driving | Serious harm | No injury | Truck and trailer mergeting in 100 kph zone almost collided with workers vehicle. Evasive action taken.
2019-31 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Stepped into a streetlight hole and sunk up to mid-thigh.
2019-32 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Walking towards door which was flung open, very close to being struck with force by the door.
2019-33 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Crushed finger while stacking materials against headboard on truck
2019-34 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Tripped on a slab in the long grass and landed on back and arm.
2019-35 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Slipped on a rock and hit knee and shoulder
2019-36 | Distribution | Employee | Electricity | Serious harm | No injury | Arcing incident from solenoid contacting generator on vehicle.
2019-37 | Distribution | Employee | Electricity | Serious harm | No injury | Arcing incident from tree blowing into lines
2019-38 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Carrying a pole which caught on something and flicked around and contacted front tooth.
2019-39 | Distribution | Employee | Driving | Serious harm | No injury | Had to take evasive action when a car continued on straight whilst indicating to turn right on the open road.
2019-40 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | No injury | Small fire started on top of truck gearbox
2019-53 | Distribution | Contractor | Electricity | Serious harm | No injury | Close-Call - While opening and then closing 11kV links 615, an unexpected long arc draw that nearly arced the entire length of the candle swing occurred. No flash over occurred.
2019-54 | Distribution | Contractor | Driving | Serious harm | Minor injury | Staff member assaulted by member of the public in road rage incident
2019-55 | Distribution | Contractor | Electricity | Serious harm | No injury | Contractor requested last min live line permit to fit cover up gears for him to complete a minor works permit for the day. NTL explained that he does not require this as under his MW he can carry out his MW while maintaining his MAD. NTL reiterated that if there was any doubt the he could not carry out his work by maintain his MAD or if there was a risk that something could occur where it meant that this was un achievable then he should not start work and that the line will need to be isolated, Earthed and he could carry out his work under a MW permit.
2019-56 | Distribution | Contractor | Electricity | Serious harm | No injury | When doing a fault, found a neutral connection to the next door property had not been connected when cable was livened.
2019-57 | Distribution | Contractor | Electricity | Serious harm | No injury | Failed to take out permit for access electrical network and left electrical network in unsafe condition.
2019-58 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | Minor injury | Arborists was struck by a falling tree branch.
2019-59 | Distribution | Contractor | Electricity | Serious harm | No injury | Contractor on checking the approved permit for run 1 he noticed a difference in the permit to his application. Contractor went onto check run 2 and found differences as well. Kelly contacted control room and discussed the findings and agreed on new IE sites
2019-60 | Distribution | Contractor | Driving | Fatality | No injury | Worker fell asleep causing loss of control of light vehicle
2019-61 | Distribution | Employee | Not listed (specify in narrative) | Fatality | No injury | Dropped/Nil phone audio during fault calls
2019-62 | Distribution | Employee | Asset failure | Serious harm | No injury | Gas bottle hose failed
2019-63 | Distribution | Employee | Asset failure | Serious harm | No injury | Head of pole broke
2019-64 | Distribution | Employee | Mobile powered plant | Serious harm | No injury | Pallets fell off forklift
2019-65 | Distribution | Employee | Electricity | Fatality | No injury | Legally Priviledged
2019-66 | Distribution | Employee | Electricity | Serious harm | No injury | Control not informed that issuer earths had been applied
2019-67 | Distribution | Employee | Work at heights | Serious harm | No injury | Potential to fall from height due to unsafe behaviours
2019-68 | Distribution | Employee | Electricity | Fatality | No injury | Contact with electricity resulting in electric shock (no injury) when replacing a fuse and fuse base in a boundary box.
2019-69 | Distribution | Contractor | Electricity | Fatality | No injury | Contractor breached MAD when cable jointing.
2019-70 | Distribution | Contractor | Electricity | Fatality | Minor injury | Contractor recevied electric shock while carrying out commissioning checks on a circuit breaker.
2019-71 | Distribution | Contractor | Electricity | Fatality | No injury | Contractor cut into live 11kV Cable, believing they were cutting into a low voltage cable. Serious near miss.
2019-73 | Distribution | Contractor | Driving | Fatality | No injury | Driver fell asleep at wheel, drifted onto the grass left hand verge.
2019-74 | Distribution | Contractor | Driving | Fatality | No injury | ATVU lost traction on descent. Driver & passenger abandoned ATVU which left track and rolled down hill.
2019-75 | Distribution | Contractor | Mobile powered plant | Fatality | No injury | Truck winch used for task not intended to use for. Truck rolled forward over chocks and down hill striking another vehicle. Secondary vehicle has rolled down embankment coming to rest next to residential property.
2019-76 | Distribution | Contractor | Driving | Fatality | No injury | Driver failed to adequately check the road was clear prior to making the u turn manoeuvre resulting in a collision with an oncoming vehicle
2019-77 | Distribution | Employee | Driving | Fatality | No injury | MOP collided with employee in 100km/h zone. Employee not at fault.
2019-78 | Distribution | Contractor | Driving | Fatality | No injury | Ute with tandem trailer lost traction and slid over bank landing on SH below property.
2019-79 | Distribution | Employee | Electricity | Fatality | No injury | No spotter, barrier or safety process was in place to make employee aware or prevent him from touching the open end of the cable.
2019-80 | Distribution | Employee | Electricity | Serious harm | No injury | Near Hit / Incorrect installation of drop out HV fuse carriers
2019-81 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Left knee hit by chain - attempting to pull the chain out from an old pole and the chain came out and hit my left knee.
2019-82 | Distribution | Employee | Electricity | Fatality | Serious harm | LV Arc Flash
2019-83 | Distribution | Employee | Driving | Fatality | No injury | Employee Using Cellphone while Driving PowerNet Vehicle
2019-84 | Distribution | Employee | Driving | Fatality | No injury | Vehicle Loss of Control
2019-85 | Distribution | Employee | Driving | Fatality | No injury | Work truck vs fence - lost control and drove down the bank and through the farmers fence.
2019-86 | Distribution | Employee | Electricity | Serious harm | No injury | Shallow Power Cables
2019-87 | Distribution | Employee | Driving | Fatality | Minor injury | Work vehicle roll over
2019-88 | Distribution | Employee | Electricity | Fatality | No injury | Potential livening of 11kV cables that disconnected and the ends cut
2019-89 | Distribution | Employee | Lone working | Serious harm | No injury | Aggressive customer grabbed and threatened an employee, whilst caring out work in isolation
2019-90 | Distribution | Employee | Electricity | Fatality | Minor injury | Shorting of LV cables in TX resulted in Arc-Flash, employee was working in close proximity to Live LV
2019-91 | Distribution | Employee | Driving | Serious harm | No injury | Ladder not secured on vehicle, ladder detached during driving falling on to the road.
2019-92 | Distribution | Employee | Work at heights | Serious harm | Minor injury | Loss of control of conductor during pole change, employee dislocated shoulder
2019-93 | Distribution | Employee | Driving | Fatality | No injury | Loss of control of vehicle resulting in a crash, distraction was the cause.
2019-94 | Distribution | Contractor | Work at heights | Fatality | No injury | Ladder on scaffold site not installed correctly, ladder moved when worker was ascending, there was no fall.
2019-95 | Distribution | Employee | Driving | Serious harm | No injury | Loss of control of line truck when 4wding, descending steep track. Truck slid off track and came to rest against a tree.
2019-96 | Distribution | Employee | Not listed (specify in narrative) | Serious harm | Minor injury | Employee fell tripped and fell down stairs.
2019-97 | Distribution | Employee | Work at heights | Serious harm | No injury | Conductor gave way when line guard was removed, could have resulted in injury due to falling objects.
2019-98 | Distribution | Employee | Hazardous materials | Serious harm | No injury | Work process not followed when removing meters from potential ACM boards.
2019-99 | Distribution | Employee | Traffic management | Fatality | No injury | Dropped conductor onto State Highway
2019-100 | Distribution | Employee | Asset failure | Serious harm | No injury | Pillar Fire Haruru - proximity to hazardous substances
2019-101 | Distribution | Contractor | Mobile powered plant | Serious harm | No injury | Reversed controls on MEWP
2019-123 | Distribution | Contractor | Hazardous materials | Serious harm | No injury | Gas Stike - Concrete cutter contacted 32mm gas pipe that had been instered into a steel pipe
2019-124 | Distribution | Contractor | Electricity | Fatality | No injury | Worker received 'tingle' across chest after a third party activated a generator during a 3 pole shutdown
2019-125 | Distribution | Contractor | Hazardous materials | Serious harm | Minor injury | A pocket of gas escaped from a ped causing the detector to alarm and read above 100ppm. Worker inhaled some gas Worker was taken to the hospital for a precautionary checkup.
2019-126 | Distribution | Contractor | Driving | Serious harm | No injury | Crew was reversing an All Terrain Vehicle (ATV), on a forest track, when the track subsided causing the ATV to tip 90 degrees on to its side.
2019-127 | Distribution | Contractor | Electricity | Fatality | No injury | Employee made contact with live cable in excavation
2019-128 | Distribution | Contractor | Electricity | Fatality | No injury | New subdivision. LV cable laid previous day. Came out to fit a link pillar and discovered the cable was live. It should not have been connected yet.
2019-129 | Distribution | Contractor | Electricity | Serious harm | Minor injury | PI was completing a demo of a service at Apirana Avenue, Glen Innes. PI isolated the service cable by removing the service fuses and then removed the service supply from the fuse carriers. So that this service does not get livened again by a third party, PI cut the service cables at ground level. PI had cut through three service cables successfully with the use of ratchet cutters and when cutting the forth cable he has somehow also cut through a live phase. This is when the incident happened and the injuries were sustained.
2019-130 | Distribution | Contractor | Electricity | Serious harm | No injury | Poor communication protocols resulted in a live switch being earthed down.
2019-131 | Distribution | Contractor | Electricity | Fatality | No injury | Arrived on site to undertake compliance checks and observed PI completing a live breach joint without wearing the correct insulated LV gloves and using a LV buzzer for testing.
2019-132 | Distribution | Contractor | Not listed (specify in narrative) | Fatality | Serious harm | A sub-contractor was performing work in a freestanding Andelect cabinet with a JW3 LV frame connected to a 300kVA transformer with exposed copper bus bar when an arc flash occurred. We would note this as critical risk of fire / explosion.
2019-133 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | Serious harm | A high voltage oil switch failed during planned switching operations. The switches oil tank ruptured and caught fire. We would note this as critical risk of fire / explosion.
2019-134 | Distribution | Contractor | Electricity | Serious harm | No injury | During a No Power Fault reported by a homeowner, the responding Fault Person discovered incorrectly disconnected wiring in a pillar by others. A live feed existed into a temporary builders supply which had had the meter removed.
2019-135 | Distribution | Contractor | Electricity | Serious harm | No injury | During reactive switching, a live feeder was earthed, resulting in overhead lines failing.
2019-136 | Distribution | Contractor | Electricity | Serious harm | No injury | 3rd party contractor excavated under live transformer and supported with timber frame.
2019-137 | Distribution | Contractor | Electricity | Fatality | No injury | 3rd party potholing for gas mains and almost struck 11kV lines.
2019-138 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | No injury | While a line truck was travelling up a steep incline, two strapped concrete poles slipped from the back of the truck onto the road. We would note this as critical risk of fall from height (people and plant).
2019-139 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | Minor injury | Job involved removing hazardous trees adjacent to HV powerlines using MEWP with traffic control. While trimming a large Pine tree MEWP operator was using a top-handled chainsaw to cut and hold branches before dropping them to ground for chipping. As operator was cutting one branch about 1 metre length with pine cones using chainsaw in left hand and holding branch with right hand the weight of the branch pulled his right hand in contact with the chainsaw causing a cut to his right thumb. Operator descended out of bucket, spoke his colleagues who dressed his wound and took him to medical centre where he received stitches. We would note this as critical risk of Struck by or striking and object.
2019-140 | Distribution | Contractor | Driving | Serious harm | No injury | While driving MEWP and chipper the truck has veered off the roadside then driver managed to get back onto the road but the chipper has spun round, disconnected from the truck pintle, somersaulted and landed up in the roadside drain.
2019-141 | Distribution | Contractor | Electricity | Fatality | No injury | Piling machine for the Northern Motorway Improvements (NCI) struck the overhead line.
2019-142 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | No injury | Transformer C-1391 erupted in flames engulfing the unit and overhead lines. We would note this as critical risk of fire / explosion.
2019-143 | Distribution | Contractor | Not listed (specify in narrative) | Serious harm | No injury | Oil switchgear failed during re livening after planned maintenance. We would note this as critical risk of fire / explosion.
2019-144 | Distribution | Contractor | Electricity | Fatality | No injury | 3rd party pulling fibre cable near 33kV cable. They had B4UDig Plans but had not requested a Standover as required for working near sub-transmission cables (detailed in the instructions with the B4UDig Plans) and not located, marked out or confirmed the location of the 33kV.
2019-145 | Distribution | Contractor | Not listed (specify in narrative) | Fatality | No injury | Person from Moving machinery walked under a suspended load (30 ton transformer). We would note this as critical risk of fall from height (people and plant).
2019-146 | Distribution | Contractor | Electricity | Fatality | No injury | Client requested a pit be relocated. After their request was not completed they took it upon themselves to move the live cable, also resulted in the earth pin being damaged.
2019-147 | Distribution | Contractor | Electricity | Serious harm | No injury | Notification by Electrix that crane operator fell asleep and slew crane into overhead 110Kv transmission lines, no visible damaged to overhead conductor or structure, line was isolated on the day of the incident.
2019-148 | Distribution | Contractor | Electricity | Serious harm | No injury | 3rd party had hit a live underground power cable with a digger.
2019-149 | Distribution | Contractor | Driving | Serious harm | No injury | Connect 8 contractor ASCO were attempting to hitch a transporter trailer up to a 6 wheel tipper truck on a hill (the trailer had been dropped of earlier in the day) the trailer had some how started to roll backwards down the hill/road. The trailer carried on, damaged a parked vehicle. The trailer continued to travel down hill until it swerved to the other side of the road where it collided with a concrete LV power pole.
2019-150 | Distribution | Contractor | Electricity | Serious harm | No injury | 3rd party removed a house without disconnecting the power, (demolition disconnect). When they removed the house this left live cables on site. Worksafe was notified of the hazard left at the site. This was reported as an unsafe work act by address only, contractor is not known. There is no follow up response from WorkSafe expected.
2019-151 | Distribution | Employee | Work-related ill-health | Serious harm | Minor injury | Lineman suffered a tear to his achilles when descending a ladder - this doesn't fit with two of the criteria as it is not serious harm or involved a critical risk from list
2019-152 | Distribution | Contractor | Work-related ill-health | Serious harm | Minor injury | Arborist suffered back strain when he slipped
2019-04 | Generation | Employee | Asset failure | Serious harm | No injury | Wairakei G7 Left Hand Emergency Stop Valve (ESV) hung up momentarily on shut down. Valve was retested on start-up and failed to move. Start-up halted and remediation work undertaken on valve. Stand-back engineering review of LP machine ESVs being undertaken.
2019-05 | Generation | Employee | Asset failure | Serious harm | No injury | G10 Right Hand Emergency Stop Valve did not close when the machine tripped. ESV hung up. Was repeatedly manually tripped by the operators but was stuck in the open position. Valve maintained and unit returned to service.Critical Safety Device Failure
2019-06 | Generation | Employee | Work at heights | Fatality | No injury | During rig up for a fishing operation on a geothermal well, an operator placed an 8kg part of the fishing tool on the scaffold around the well head. While the operator descended from the access ladder to the scaffold, the tool rolled off the scaffold platform and dropped approximately 3 meters and hit the slickline sheave at ground level. It was found that despite the kick board had not been installed (where the tool fell) & other safety issues, the scaffold had been incorrectly signed off as safe.
2019-07 | Generation | Employee | Not listed (specify in narrative) | Serious harm | No injury | K-line steam piping was found to have a section flooded with cold condensate water as a result of a blocked drain. The cold water poses a significant risk of causing of severe pressure collapse and in and failure of the pipeline if it comes into contact and condenses steam in the line. Access to area restricted and system was held in steady state. Work was slowly undertaken to warm and remove the water without altering the interface between steam and water. Plant needed to operate outside its design conditions during this process.
2019-08 | Generation | Contractor | Hazardous materials | Serious harm | No injury | Contractors were engaged to carry out remedial works on a geothermal bleedline. During this work they carried out work outside of the permit when they used a disc grinder to cut into a pressurised gas line which led to H2S gas being released.
2019-41 | Generation | Employee | Hazardous materials | Fatality | No injury | Rotokawa geothermal - pentane leak while replacing mechanical seal
2019-42 | Generation | Employee | Driving | Fatality | Minor injury | Road - Vehicle forced off road by oncoming public vehicle
2019-43 | Generation | Employee | Driving | Fatality | No injury | Road - Had to take evasive action to avoid oncoming public vehicle
2019-44 | Generation | Contractor | Hazardous materials | Fatality | No injury | Mokai geothermal - Pentane spill to ground when RASM not applied
2019-45 | Generation | Employee | Electricity | Fatality | No injury | Ngatamariki geothermal - Incorrect identification of lube oil fan to be worked on
2019-46 | Generation | Employee | Asset failure | Fatality | No injury | a turbine had a low speed lock in place preparing for a gearbox removal early the week after. The following week, technicians found rotor bolts in the ground, on the hardstand and surrounding paddock. The rotor lock failed in wind speeds above 13m/s over the weekend.
2019-47 | Generation | Employee | Work at heights | Fatality | No injury | During height training at Te Apiti a Petzal I'D descender opened as a trainee went over the edge of the Turbine. It is believed his back up device rubbed against the black swinging lock on the carabiner attachment allowing the swinging gold cheek/plate of the I'D to open. The trainee was brought back to the top of the turbine where his I’D was inspected and re-secured. During the second descent the I'D once again released. The trainee, with the support of the trainer, were able to lower him slowly to the ground.
2019-48 | Generation | Employee | Work at heights | Serious harm | No injury | Walking on top of Unit 2 rotor under a Test Permit with a full penstock. Isolations were in place however do not prevent the rotor from turning as result of wicket gate leak.
2019-49 | Generation | Contractor | Not listed (specify in narrative) | Serious harm | Serious harm | Rotating Plant Critical Risk. Contractor was moving across nacelle when he lost his footing and tripped, reaching out to brace himself the index finger of his left hand made contact with high speed brake disc. After being admitted to hospital it was confirmed the fingertip could not be reattached.
2019-50 | Generation | Contractor | Electricity | Fatality | No injury | Work was being completed in a switchboard with live cables at Aviemore by a contractor. While a cable was being pushed through a hole it fell more quickly than anticipated and connected with a live conductor causing a flashover. The plant did not trip, protection did not operate and there was no injury.
2019-51 | Generation | Contractor | Driving | Fatality | No injury | A scaffolding contractor was travelling to site to commence establishment of a project on a foggy morning. The driver lost sight of the road and when he applied the brakes (travelling at approx. 55km/h) the trailer he was towing came around causing the truck to hit the curb and rollover. The driver was shaken but unharmed. Fire brigade and Police attended the event.
2019-52 | Generation | Contractor | Not listed (specify in narrative) | Serious harm | Serious harm | Contractor using a mechanical winch to hoist a tool bag. Fingers on the left hand became trapped in the winch mechanism causing lacerations and factures to multiple fingers.
2019-72 | Generation | Contractor | Not listed (specify in narrative) | Serious harm | Serious harm | No critical risk was involved. Contractor rolled his ankle on flat solid ground (with a little shingle on it). Both contractors were returning to the vehicle along the edge of the grass. Robert suddenly fell to the ground in moderate pain. It is suspected Robert slipped on small stones that rolled under his foot on the hard dry ground. Ian remarked he heard a crack as Robert fell. Robert was unable to move; his leg was not weight bearing. Tim Hope, the Orchard Manager for El Pedegru Orchard arrive. Ian called for an ambulance and proceeded to the intersection of Fraser Road and Stroad Road to meet the ambulance and escort them to Robert. Tim stayed with Robert until the ambulance arrived. Went in for surgery yesterday (25 March). Fitted plates to both the fibula and tibia just above the ankle. The third bone fracture is expected to heal naturally. Relocated ankle as it had dislocated and removed a bone fragment. All good! Initially I thought my knee failed first however, in hindsight and after discussing with surgeons the force exerted on the ankle with a dislocated knee would be insufficient to fracture the ankle so dramatically. The foot slipping sideways would have fractured and dislocated the ankle followed by the knee not supporting the weight of me falling, hence the patella dislocating as a secondary injury.
2019-111 | Generation | Employee | Driving | Fatality | No injury | Driving north on SH1 Taupo bypass in clear fine weather at 95km/h. Noticed large cloud of localized geothermal fog covering slip road exit from SHI bypass to Broadlands road. Slowed down for fog then moved into exit lane once in fog cloud. Had to brake hard as other vehicle had stopped in lane. Slowed and stopped vehicle fine but car following behind was too close and locked up brakes to avoid hitting my vehicle (no collision).
2019-112 | Generation | Contractor | Electricity | Fatality | No injury | During the removal of cables, an incorrect cable was identified and cut. The cable was potentially live as it was still connected at both ends from the control panel to generator governor Panel. The cable normally contains a 110VAC frequency loop. No electric shock was reported. Post cutting, the cable termination was removed from each end and put into terminal connectors for safety of others. Fuses have now been tested and found to have blown. The neutral screen had protected the person from receiving an electric shock.
2019-113 | Generation | Contractor | Electricity | Fatality | Minor injury | Cover of panel in generator removed to rewire 24 volt DC terminals, when contractor brushed live AC terminals and received electric shock to hand.
2019-114 | Generation | Employee | Hazardous materials | Fatality | No injury | Discovery of asbestos fibres in dust within basement of station - generator also circulates air from basement in to station.
2019-115 | Generation | Employee | Not listed (specify in narrative) | Fatality | No injury | Small Scrub fire was started due to a welding spark whilst erecting webforage safety barriers. The fire sentry used a by 20litre fire extinguisher to extinguish the flames which burnt a 2m square area of dry grass within 10-15 seconds. Although the WSSP had been completed in the morning pre work commencing with the fire risk identified and mitigations in place, the weather conditions changed rapidly after lunch. Noth west wind increased which funnelled up the pennstock slope, drying the existing fuel source and making conditions borderline for the first aid fire fighting appliances present. Work should have stopped at this point and a reassessment undertaken. Although the first aid appliance managed to extinguish the fire, 30 seconds more and the fire would have been too big to manage.
2019-116 | Generation | Contractor | Mobile powered plant | Fatality | No injury | Station overhead crane was out on Permit for major overhaul with no-go zone (Barriers) established below the crane. The lead contractor opened the station loading bay door to load vehicle, in doing so creating an opening in the work-zone barrier. Technician contractor entered restricted work zone.
2019-117 | Generation | Contractor | Mobile powered plant | Serious harm | No injury | A new digger operator was transferring soil from up slope to a down slope location while the digger was positioned on uneven ground. As the machine swiveled to face down slope it became unstable and began to topple. The digger operator immediately dropped the digger bucket to prevent any further movement. However, the angled position of the digger meant it had one track unable to get traction. The digger operator tried to re-position the machine to firmer ground by using a combination of the remaining tractable track in conjunction with a dragging motion using the bucket and boom. The operator was asked to shut down the engine and exist the machine.
2019-118 | Generation | Contractor | Driving | Serious harm | No injury | A Moxy operator was driving the articulated dump vehicle along a straight but highly cambered section of an access track when the rear wheels slid sideways on soft wet ground and then caught on hard surface. The sudden stop of the slide caused the Moxy to lurch to the left becoming unstable and flop onto its side. The load of roading gravel discharged from the box bed and onto the ground. There was no damage to equipment or injury to the operator (he was buckled into the seat harness).
2019-119 | Generation | Contractor | Driving | Serious harm | No injury | ruck dropping off material, driver applied handbrake and got out of truck but truck started to move. Driver jumped back into truck and applied brake.
2019-120 | Generation | Employee | Driving | Fatality | No injury | Employees were driving in each of their vehicles, entering access road to power station. The road is gravel so speed is restricted to 30km/ph when a speeding tanker came around a bend and forced one employees to drive into the water table ditch and the other to take evasive action.
2019-121 | Generation | Contractor | Driving | Fatality | No injury | Contractor was using Trustpower vehicle and a trailer to drop off culvert pipes. The trailer coupling became dislodged but was equipped with two robust safety chains.
2019-122 | Generation | Employee | Driving | Fatality | No injury | Driving home from work, had a couple of blinky eye periods earlier, but pushed on, then fell asleep and drove off the road about 4m before waking up. Hauled the truck back on to the road without looking, 4 wheel drift into the opposite lane then slowly corrected to the left lane. The car which was following came to see if I was OK when I had stopped.
2019-102 | Transmission | Contractor | Driving | Serious harm | No injury | A ute undertaking a U-turn on the open road was struck by a following vehicle. Fortunately, nobody was hurt, but people in both vehicles could have been seriously hurt.
2019-103 | Transmission | Contractor | Not listed (specify in narrative) | Fatality | Minor injury | Helicopter dropped one skid on a steep ridge to unload line maintenance gear. A strong tail wind gust occurred at the same time the crew member re-boarded the empty helicopter, unbalancing it. The pilot immediately lifted off, with the toe of the skid catching and breaking two high tensile wires in the nearby stock fence. The helicopter flew towards two linemen on the ground, who took evasive action. One of the lineman fell and strained his back in the process, but fortunately was not seriously injured.
2019-104 | Transmission | Employee | Driving | Serious harm | No injury | A near miss occurred when driving between Twizel & Waitaki (Sailor Cutting). An oncoming car crossed the centre line on a curve, turning into a roadside observation area overlooking Lake Benmore. The Transpower driver had to take evasive action to avoid a head-on collision
2019-105 | Transmission | Contractor | Not listed (specify in narrative) | Serious harm | No injury | A subcontractor at the Kawerau substation was attempting to move a redundant 20 tonne transformer using a traverser trolley. There was an uncontrolled movement of the transformer which caused the trolley to move away and resulted in the transformer partially tipping over. No one was injured, however there was one person nearby at the time of the incident. Early indications are that planning and change management were key factors in this incident.
2019-106 | Transmission | Contractor | Electricity | Serious harm | No injury | A hiab was unloading a portacom from a truck at an Auckland commercial site below overhead 220kV lines. During the lift the hiab came into close contact with a conductor, resulting in a flashover and tripping of the circuit. Fortunately, the operator was not injured, and the hiab suffered no significant damage.
2019-107 | Transmission | Contractor | Electricity | Serious harm | No injury | While walking across the switchyard Electrix’s lead technician observed a Delta linesman preparing to remove an earth from the Aurora take off area. He commented to the worker that it was part of his Assurance from Aurora, the linesman had been requested to take down the earth by the Aurora control room. The earth removal was stopped under the technicians’ instruction before any earths were removed, the Aurora control room was contacted and the work officially stopped.
2019-108 | Transmission | Contractor | Electricity | Serious harm | No injury | While preparing for a single span earthwire replacement pull, the old earthwire broke outside of both the primary and secondary rigging. The earthwire landed across the below 110kV HEN-MPE-A line which resulted in a fault on two circuits and a loss of supply.
2019-109 | Transmission | Contractor | Not listed (specify in narrative) | Serious harm | Serious harm | A vegetation worker received a severe lacteration to his thumb after the chainsaw he was using contacted his other hand, causing the cut to his thumb. He has undergone an operation and is recovering.
2019-110 | Transmission | Contractor | Electricity | Serious harm | Minor injury | A contractor was repositioning a cable from one MCCB to another. He moved an in-service cable back to create room for the cable migration and in doing so caused a flashover. The employee sustained a burn to his finger.